## Sheet1
Number | Doc Tag Name | My Tag Name | Doc Description | My description
0 | PURIFY_ACTIVE_TTL_DY | PUR_ACT_TTL_DY_ACC | Count of total days in purification | COUNTER The number of total elapsed purification days for the process equipment
1 | PURIFY_ACTIVE_TTL_HR | PUR_ACT_TTL_HR_ACC | Elapsed hours in current day of purification | COUNTER The number of total elapsed purification hours for the process equipment
2 | PURIFY_ACTIVE_MINUTE | PUR_ACT_MIN_ACC | Elapsed minutes in current hour of purification | COUNTER The number of elapsed purification minutes for the current ADS (60 min)
3 | PURIFY_ACTIVE_HOURS | PUR_ACT_HR_ACC | Elapsed hours in current purify cycle | COUNTER The number of elapsed purification hours for the current ADS
4 | REGEN_VENT_TIMER | RG_VENT_TMR_ACC | Elapsed seconds in regen vent 1 step | TIMER Regen Vent (seconds)
5 | REGEN_REDUC_MINUTE | RG_REDUC_MIN_ACC | Elapsed minutes in regen H2 reduction step | COUNTER Regen The number of minutes which the regen reduc runs
6 | REGEN_PURGE_MINUTES | RG_PURG_MIN_ACC | Elapsed minutes in regen hot purge step | COUNTER Regen THe number of minutes the purge step runs
7 | REGEN_COOL_MINUTE | RG_COOL_MIN_ACC | Elapsed minutes in regen cool step | COUNTER Regen the number of minutes for which the bed has cooled
8 | REGEN_VENT_2_TMR | RG_VENT_2_TMR_ACC | Elapsed seconds in regen vent 2 step
9 | REGEN_EQUALIZE_MIN | RG_EQL_MIN_ACC | Elapsed minutes in equalize step
10 | PURIFY_OVERLAP_TIMER | PUR_OVL_TMR_ACC | Elapsed seconds in Overlap step | TIMER Purify Overlap
11 | REGEN_STATE | RG_STAT_ | Number of regen step/state | STATE The current state of the regen process
12 | INLET_PX_PRESSURE | INLET_PX_PSIG_ | Option: inlet gas pressure
13 | OUTLET_PX_PRESSURE | OUTLET_PX_PSIG_ | Option: outlet gas pressure
14 | MIX_PANEL_PRESSURE | MIX_PANEL_PSIG_ | H2 gas pressure
15 | MFM_FLOW | MFM_FLOW_ | Option: mass flow meter
16 | ADS_A_BED_TEMP_READ | ADS_A_BED_TEM_RD_ | Adsorber A vessel bed temperature TC6
17 | ADS_A_WALL_TEMP_READ | ADS_A_WALL_TEM_RD_ | Adsorber A vessel wall temperature TC7
18 | ADS_B_BED_TEMP_READ | ADS_B_BED_TEM_RD_ | Adsorber B vessel bed temperature TC8
19 | ADS_B_WALL_TEMP_READ | ADS_B_WALL_TEM_RD_ | Adsorber B vessel wall temperature TC9
20 | ADS_PH_GAS_TEMP_READ | ADS_PH_GAS_TEM_RD_ | Adsorber A/B preheater gas temperature TC10
21 | ADS_PH_ROD_TEMP_READ | ADS_PH_ROD_TEM_RD_ | Adsorber A/B preheater wall temperature TC11
22 | PREHEATER_SP | PREHEATER_SP_ | Adsorber Preheater Setpoint | CONTROL Preheater PID Setpoint
23 | ADS_PH_PID_DATA | ADS_PH_PID_DT_CVP | Ads Preheater Dutycycle Output | PID ADS Preheater
24 | BLANKET_SP | BLANKET_SP_ | Adsorber Blanket Setpoint | CONTROL Blanket PID Setpoint
25 | ADS_A_BLKT_PID_DATA | ADS_A_BKT_PID_DT_CVP | Adsorber A Blanket Dutycycle Output | PID ADS A Blanket
26 | ADS_B_BLKT_PID_DATA | ADS_B_BKT_PID_DT_CVP | Adsorber B Blanket Dutycycle Output | PID ADS B Blanket
27 | HRS_LEFT_IN_PURIFY | HRS_LEFT_IN_PUR_ | Remaining hours in purify
28 | MIN_LEFT_IN_PURIFY | MIN_LEFT_IN_PUR_ | Remaining minutes in purify
29 | REGEN_HRS_LEFT | RG_HRS_LEFT_ | Remaining hours in regen | STATUS Regen Preheater Temperature Initial Temperature
30 | REGEN_MIN_LEFT | RG_MIN_LEFT_ | Remaining minutes in regen | STATUS Preheater Alarm Measured temperature change
31 | TOTAL_FLOW | TOTAL_FLOW_ | Accumulated flow volume (option, lower bits)
32 | TOTAL_FLOW | TOTAL_FLOW_ | Accumulated flow volume (option, upper bits)
1440 | MB_HEARTBEAT_ON | MB_HB_ON_EN | Communications heartbeat
1441 | SYSTEM_ALARM_FLAG | SYSTEM_ALM_FLAG_ | Alarm has stopped the system
1442 | REGEN_ALARM_FLAG | RG_ALM_FLAG_ | Alarm has interrupted the regen process
1443 | PURIFY_ALARM_FLAG | PUR_ALM_FLAG_ | Alarm has interrrupted the purify process
1444 | WARNING |  | SYSTEM, REGEN, or PURIFY Warning
1445 | SYSTEM_STANDBY | SYSTEM_STANDBY_ | System is in standby | STATE System Standby
1446 | PURIFY_MANUAL_HOLD | PUR_MANUAL_HOLD_ | Manual purify hold command | STATE Purify Manual Hold
1447 | SET_REGEN_HOLD | SET_RG_HOLD_ | Manual regen hold command
1448 | EMO_ACTIVE | EMO_ACT_ | Emergency stop is active | STATUS The EMO has been depressed
1449 | PROC_PURIFY_A | PROC_PUR_A_ | Bed A is purifying | STATE Process Purify A
1450 | PROC_PURIFY_B | PROC_PUR_B_ | Bed B is purifying | STATE Process Purify B
1451 | ALARM_RELAY_CONFIG | ALM_RLY_CONFIG_ | Alarm relay configuration (1 = failsafe, 0 = standard)
|  | IF_OFF_TURN_OFF_ | Blank output | If this is off, go ahead and turn it off
|  | IF_OFF_TURN_OFF_ |  | If this is off, go ahead and turn it off
|  | IF_OFF_TURN_OFF_ |  | If this is off, go ahead and turn it off
|  | IF_OFF_TURN_OFF_ |  | If this is off, go ahead and turn it off
1456 | ADS_A_REGEN_IN_OUT | ADS_A_RG_IN_OUT_ | AV1/AV6 OPEN - Adsorber A regeneration gas outlet/inlet valve | SV-1A AV1A/AV6A OPEN
1457 | ADS_A_PURIFY_OPEN | ADS_A_PUR_OPEN_ | AV2/AV7 OPEN - Adsorber A process gas inlet/outlet valve | SV-2A AV2A/AV7A OPEN
1458 | ADS_B_PURIFY_OPEN | ADS_B_PUR_OPEN_ | AV3/AV8 OPEN - Adsorber B process gas inlet/outlet valve | SV-3A AV3A/AV8A OPEN
1459 | ADS_B_REGEN_IN_OUT | ADS_B_RG_IN_OUT_ | AV4/AV9 OPEN - Adsorber B regeneration gas outlet/inlet valve | SV-4A AV4A/AV9A OPEN
1460 | BYPASS_VALVE | BYPASS_VLV_ | SV-5 Bypass (AUTO: closed, PMAN: open) | SV-5
1461 | H2_INLET_VALVE | H2_INLET_VLV_ | AV-10 OPEN - H2 Mixing Panel Valve | SV-6A AV10A OPEN
1462 | PROC_GAS_INLET_VALVE | PROC_GAS_INLET_VLV_ | AV-11 OPEN - Process Gas Mixing Panel Valve | SV-7A AV11A OPEN
1463 | EQUALIZE_VALVE | EQL_VLV_ | AV-20 OPEN - Equalize valve | SV-9A AV13A OPEN
1464 | ADS_A_PURIFY_CLOSE | ADS_A_PUR_CLOSE_ | AV2/AV7 CLOSE - Adsorber A process gas inlet/outlet valve | SV-2B AV2B/AV7B CLOSE
1465 | ADS_B_PURIFY_CLOSE | ADS_B_PUR_CLOSE_ | AV3/AV8 CLOSE - Adsorber B process gas inlet/outlet valve | SV-3B AV3B/AV8B CLOSE
1468 | ALARM_BUZZER_OUT | ALM_BUZZER_OUT_ | Alarm Buzzer | ALARM Buzzer Output
1469 | Watchdog | WATCHDOG_ | Watchdog | K7
1470 | Alarm Relay | ALM_RLY_ | Alarm relay (configurable as failsafe or standard) | K8
1471 | Gas Relay | GAS_RLY_ | Gas relay | K9
1472 | ADS_PH_CONTACTOR | ADS_PH_CTR_ | K1 - not used for purifier sizes < 400
1473 | ADS_A_BLKT_CONTACTOR | ADS_A_HEAT_CTR_ | K2 - sizes < 400 controls common PH and A BLKT
1474 | ADS_B_BLKT_CONTACTOR | ADS_B_HEAT_CTR_ | K3 - sizes < 400 controls common PH and B BLKT
1478 | ADS_PREHEATER_SSR | ADS_PREHEATER_SSR_ | SSR1
1479 | ADS_BLANKET_SSR | ADS_BLANKET_SSR_ | SSR2
1488 | EXOTHERM_ALARM | EXOTHERM_ALM_ | Purify High Temp alarm
1489 | PLC_FAULT_ALARM | PLC_FAULT_ALM_ | Major PLC Fault alarm
1490 | UPS_FAULTED_ALARM | UPS_FAULTED_ALM_ | Uninterrupted Power Supply failure alarm
1497 | LOW_PLC_BATTERY_ALM | LOW_PLC_BATT_ALM_ | Low PLC Battery alarm | ALARM System Low PLC Battery
1498 | GFI_TRIPPED_ALARM | GFI_TRIPPED_ALM_ | GFI Tripped alarm | ALARM System GFI Tripped
1499 | MAIN_PWR_ALARM | MAIN_PWR_ALM_ | Main Power Fail alarm | ALARM System Main Power Fail
1500 | CTL_PWR_ALARM | CTL_PWR_ALM_ | Control Power Fail alarm | ALARM System Control Power Fail
1501 | LP_OUTLET_GAS_ALARM | LP_OUTLET_GAS_ALM_ | High Gas Pressure alarm
1502 | LP_INLET_GAS_ALARM | LP_INLET_GAS_ALM_ | Low Gas Pressure alarm | ALARM System Low Gas Pressure
1503 | HP_INLET_GAS_ALARM | HP_INLET_GAS_ALM_ | Gas Inlet High Pressure alarm | ALARM Gas Inlet High Pressure
1504 | HP_OUT_GAS_ALARM | HP_OUT_GAS_ALM_ | Gas Outlet High pressure alarm | ALARM Gas Outlet High Pressure
1505 | OPEN_PX1_ALARM | OPEN_PX1_ALM_ | Gas Inlet PX open alarm | ALARM Gas Inlet Pressure Transmitter Broken
1506 | OPEN_PX2_ALARM | OPEN_PX2_ALM_ | Gas Outlet PX open alarm | ALARM Gas Outlet Pressure Transmitter Broken
1508 | SAFETY_VENT_ALARM | SAFETY_VENT_ALM_ | Overpressure Event alarm
1509 | FLAME_FAULT_ALARM | FLAME_FAULT_ALM_ | Flame sensot fault alarm
1510 | FLAME_DETECTED_ALARM | FLAME_DETECTED_ALM_ | Flame detected alarm
1520 | PURIFY_HOLD_ALARM | PUR_HOLD_ALM_ | System Purify Hold alarm | ALARM System Purify Hold
1521 | LT_INLET_GAS_ALARM | LT_INLET_GAS_ALM_ | Inlet Low Temperature alarm
1536 | HTI_ALARM | HTI_ALM_ | High Temp Interlock alarm | ALARM High Temperature Interlocks
1537 | PH_FAULT_ALARM | PH_FAULT_ALM_ | Preheater Failed to Heat alarm | ALARM Preheater Fault
1538 | H2_LEVEL_ALM | H2_LEVEL_ALM_ | Hydrogen level alarm
1539 | OPEN_PX_3_ALARM | OPEN_PX3_ALM_ | Blend Station Open PX alarm
1540 | LP_BLEND_GAS_ALARM | LP_BLEND_GAS_ALM_ | Low Pressure Blend Gas alarm
1541 | HP_BLEND_GAS_ALARM | HP_BLEND_GAS_ALM_ | High Pressure Blend Gas alarm
1542 | BLEND_GAS_LEAK_ALARM | BLEND_GAS_LEAK_ALM_ | Blend Gas Leak Detected alarm
1543 | LOW_REG_PW_DEV_ALARM | LOW_REG_PW_DEV_ALM_ | Regen Low Power Deviation alarm
1544 | HI_REG_PW_DEV_ALARM | HI_REG_PW_DEV_ALM_ | Regen High Power Deviation alarm
1545 | LP_EXT_PNEU_ALARM | LP_EXT_PNEU_ALM_ | Low External Pneumatic Pressure alarm | ALARM System Pneumatic Pressure Low
1546 | LP_INT_PNEU_ALARM | LP_INT_PNEU_ALM_ | Low Internal Pneumatic Pressure alarm
1547 | REG_COOL_FAIL_ALARM | REG_COOL_FAIL_ALM_ | Regen Cooling Failure alarm
1548 | OPEN_TC10_ALARM | OPEN_TC10_ALM_ | Open TC10 on Preheater Gas alarm
1549 | OPEN_TC11_ALARM | OPEN_TC11_ALM_ | Open TC11 on Preheater Rod alarm
1550 | HT_PH_GAS_ALARM | HT_PH_GAS_ALM_ | High Temp Preheater Gas alarm
1551 | HT_PH_ROD_ALARM | HT_PH_ROD_ALM_ | High Temp Preheater Rod alarm
1553 | OPEN_TC6_ALARM | OPEN_TC6_ALM_ | Adsorber A Bed TC6 Open alarm | ALARM Adsorber A Bed Thermocouple Open
1555 | OPEN_TC7_ALARM | OPEN_TC7_ALM_ | Adsorber A Wall TC7 Open alarm | ALARM Adsorber A Wall Thermocouple Open
1557 | HT_WALL_ADS_A_ALARM | HT_WALL_ADS_A_ALM_ | Adsorber A Regen Wall High Temp alarm | ALARM ADS A REGEN Wall High Temp
1558 | LT_BED_ADS_A_ALARM | LT_BED_ADS_A_ALM_ | Adsorber A Bed Low Temp alarm | ALARM ADS A Wall Low Temperature
1559 | ADS_A_EXOTHERM_ALARM | ADS_A_EXOTHERM_ALM_ | Adsorber A Purify High Temp alarm | ALARM ADS A Purify High Temp
1560 | HT_BED_ADS_A_ALARM | HT_BED_ADS_A_ALM_ | Adsorber A Bed High Temp alarm
1585 | OPEN_TC8_ALARM | OPEN_TC8_ALM_ | Adsorber B Bed TC8 Open alarm | ALARM Adsorber B Bed Thermocouple Open
1587 | OPEN_TC9_ALARM | OPEN_TC9_ALM_ | Adsorber B Wall TC9 Open alarm | ALARM Adsorber B Wall Thermocouple Open
1589 | HT_WALL_ADS_B_ALARM | HT_WALL_ADS_B_ALM_ | Adsorber B Regen Wall High Temp alarm | ALARM ADS B REGEN Wall High Temp
1590 | LT_BED_ADS_B_ALARM | LT_BED_ADS_B_ALM_ | Adsorber B Bed Low Temp alarm | ALARM ADS B Wall Low Temperature
1591 | ADS_B_EXOTHERM_ALARM | ADS_B_EXOTHERM_ALM_ | Adsorber B Purify High Temp alarm | ALARM ADS B Purify High Temp
1592 | HT_BED_ADS_B_ALARM | HT_BED_ADS_B_ALM_ | Adsorber B Bed High Temp alarm
1600 | SCREEN_COMMS_ERROR | SCREEN_COMMS_ERR_ | Communication error between HMI and PLC warning
1602 | UPS_FAULTED_WARN | UPS_FAULTED_WRN_ | Uninterrupted Power Supply failure warning
1609 | LOW_PLC_BATTERY_WARN | LOW_PLC_BATT_WRN_ | Low PLC Battery warning | WARNING System Low PLC Battery
1610 | GFI_TRIPPED_WARN | GFI_TRIPPED_WRN_ | GFI Tripped warning | WARNING System GFI Tripped
1611 | MAIN_PWR_WARN | MAIN_PWR_WRN_ | Main Power Fail warning | WARNING System Control Power Fail
1612 | CTL_PWR_WARN | CTL_PWR_WRN_ | Control Power Fail warning | WARNING System Control Power Fail
1613 | LP_OUTLET_GAS_WARN | LP_OUTLET_GAS_WRN_ | High Gas Pressure warning
1614 | LP_GAS_WARN | LP_INLET_GAS_WRN_ | Low Gas Pressure warning | WARNING System Low Gas Pressure
1615 | HP_INLET_GAS_WARN | HP_INLET_GAS_WRN_ | Gas Inlet High Pressure warning | WARNING Gas Inlet High Pressure
1616 | HP_OUT_GAS_WARN | HP_OUT_GAS_WRN_ | Gas Outlet High Pressure warning | WARNING Gas Outlet High Pressure
1617 | OPEN_PX1_WARN | OPEN_PX1_WRN_ | Gas Inlet PX open warning | WARNING Gas Inlet Pressure Transmitter Broken
1618 | OPEN_PX2_WARN | OPEN_PX2_WRN_ | Gas Outlet PX open warning | WARNING Gas Outlet Pressure Transmitter Broken
1620 | SAFETY_VENT_WARN | SAFETY_VENT_WRN_ | Overpressure Event warning
1629 | MODBUS_ERROR | MODBUS_ERR_ | ModBus Error
1632 | PURIFY_HOLD_WARN | PUR_HOLD_WRN_ | System Purify Hold warning | WARNING System Purify Hold
1633 | LT_INLET_GAS_WARN | LT_INLET_GAS_WRN_ | Inlet Low Temperature warning
1648 | HTI_WARN | HTI_WRN_ | High Temp Interlock warning | WARNING High Temperature Interlocks
1649 | PH_FAULT_WARN | PH_FAULT_WRN_ | Preheater Failed to Heat warning | WARNING Preheater Fault
1650 | H2_LEVEL_WARN | H2_LEVEL_WRN_ | Hydrogen level warning
1651 | OPEN_PX3_WARN | OPEN_PX3_WRN_ | Blend Station Open PX warning
1652 | LP_BLEND_GAS_WARN | LP_BLEND_GAS_WRN_ | Low Pressure Blend Gas warning
1653 | HP_BLEND_GAS_WARN | HP_BLEND_GAS_WRN_ | High Pressure Blend Gas warning
1654 | BLEND_GAS_LEAK_WARN | BLEND_GAS_LEAK_WRN_ | Blend Gas Leak Detected warning
1655 | LOW_REG_PW_DEV_WARN | LOW_REG_PW_DEV_WRN_ | Regen Low Power Deviation warning
1656 | HI_REG_PW_DEV_WARN | HI_REG_PW_DEV_WRN_ | Regen High Power Deviation warning
1657 | LP_EXT_PNEU_WARN | LP_EXT_PNEU_WRN_ | Low External Pneumatic Pressure warning | WARNING System Pneumatic Pressure Low
1658 | LP_INT_PNEU_WARN | LP_INT_PNEU_WRN_ | Low Internal Pneumatic Pressure warning
1659 | REG_COOL_FAIL_WARN | REG_COOL_FAIL_WRN_ | Regen Cooling Failure warning
1660 | OPEN_TC10_WARN | OPEN_TC10_WRN_ | Open TC10 on Preheater Gas warning
1661 | OPEN_TC11_WARN | OPEN_TC11_WRN_ | Open TC11 on Preheater Rod warning
1662 | HT_PH_GAS_WARN | HT_PH_GAS_WRN_ | High Temp Preheater Gas warning
1663 | HT_PH_ROD_WARN | HT_PH_ROD_WRN_ | High Temp Preheater Rod warning
1665 | OPEN_TC6_WARN | OPEN_TC6_WRN_ | Adsorber A Bed TC6 Open warning | WARNING Adsorber A Bed Thermocouple Open
1667 | OPEN_TC7_WARN | OPEN_TC7_WRN_ | Adsorber A Wall TC7 Open warning | WARNING Adsorber A Wall Thermocouple Open
1669 | HT_WALL_ADS_A_WARN | HT_WALL_ADS_A_WRN_ | Adsorber A Regen Wall High Temp warning | WARNING ADS A Wall High Temperature
1670 | LT_BED_ADS_A_WARN | LT_BED_ADS_A_WRN_ | Adsorber A Bed Low Temp warning | WARNING ADS A Wall Low Temperature
1671 | ADS_A_EXOTHERM_WARN | ADS_A_EXOTHERM_WRN_ | Adsorber A Purify High Temp warning | WARNING ADS A Purify High Temp
1672 | HT_BED_ADS_A_WARN | HT_BED_ADS_A_WRN_ | Adsorber A Bed High Temp warning
1681 | OPEN_TC8_WARN | OPEN_TC8_WRN_ | Adsorber B Bed TC8 Open warning | WARNING Adsorber B Bed Thermocouple Open
1683 | OPEN_TC9_WARN | OPEN_TC9_WRN_ | Adsorber B Wall TC9 Open warning | WARNING Adsorber B Wall Thermocouple Open
1685 | HT_WALL_ADS_B_WARN | HT_WALL_ADS_B_WRN_ | Adsorber B Regen Wall High Temp warning | WARNING ADS B Wall High Temperature
1686 | LT_BED_ADS_B_WARN | LT_BED_ADS_B_WRN_ | Adsorber B Bed Low Temp warning | WARNING ADS B Wall Low Temperature
1687 | ADS_B_EXOTHERM_WARN | ADS_B_EXOTHERM_WRN_ | Adsorber B Purify High Temp warning | WARNING ADS B Purify High Temp
1688 | HT_BED_ADS_B_WARN | HT_BED_ADS_B_WRN_ | Adsorber B Bed High Temp warning
1696 | LP_REGEN_ALM | LP_RG_ALM_ | Low Pressure Regen Alarm
1712 | LP_REGEN_WRN | LP_RG_WRN_ | Low Pressure Regen Warning