## Sheet1
Number | Doc Tag Name | My Tag Name | Doc Description | My description
0 | PURIFY_ACTIVE_TTL_DY | PUR_ACT_TTL_DY_ACC | Count of total days in purification | COUNTER The number of total elapsed purification days for the process equipment
1 | PURIFY_ACTIVE_TTL_HR | PUR_ACT_TTL_HR_ACC | Elapsed hours in current day of purification | COUNTER The number of total elapsed purification hours for the process equipment
2 | PURIFY_ACTIVE_MINUT | PUR_ACT_MIN_ACC | Elapsed minutes in current hour of purification | COUNTER The number of elapsed purification minutes for the current ADS (60 min)
3 | PURIFY_ACTIVE_HOURS | PUR_ACT_HR_ACC | Elapsed hours in current purify cycle | COUNTER The number of elapsed purification hours for the current ADS
4 | REGEN_VENT_TIMER | RG_VENT_TMR_ACC | Elapsed seconds in regen vent step | TIMER Regen Vent (seconds)
5 | REGEN_REDUC_MINUTE | RG_REDUC_MIN_ACC | Elapsed minutes in regen H2 reduction step | COUNTER Regen The number of minutes which the regen reduc runs
6 | REGEN_PURGE_MINUTES | RG_PURG_MIN_ACC | Elapsed minutes in regen hot purge step | COUNTER Regen THe number of minutes the purge step runs
7 | REGEN_COOL_MINUTE | RG_COOL_MIN_ACC | Elapsed minutes in regen cool step | COUNTER Regen the number of minutes for which the bed has cooled
8 | REGEN_EQUALIZE_MIN | RG_EQL_MIN_ACC | Elapsed minutes in equalize step
9 | PURIFY_OVERLAP_TIMER | PUR_OVL_TMR_ACC | Elapsed seconds in Overlap step | TIMER Purify Overlap
10 | REGEN_STATE | RG_STAT_ | Number of regen step/state | <datalog> STATE The current state of the regen process
11 | PX1 | INLET_PX_PSIG_ | Option: Inlet gas pressure
12 | PX2 | OUTLET_PX_PSIG_ | Option: Outlet gas pressure
13 | PX3 | MIX_PANEL_PSIG_ | H2 gas pressure | <datalog>
14 | MFM1 | MFM_FLOW_ | Option: Mass Flow | <datalog>
15 | TC6 | ADS_A_BED_TEM_RD_ | Adsorber A vessel bed temperature | <datalog>
16 | TC7 | ADS_A_WALL_TEM_RD_ | Adsorber A vessel wall temperature | <datalog>
17 | TC8 | ADS_B_BED_TEM_RD_ | Adsorber B vessel bed temperature | <datalog>
18 | TC9 | ADS_B_WALL_TEM_RD_ | Adsorber B vessel wall temperature | <datalog>
19 | TC10 | ADS_PH_GAS_TEM_RD_ | Adsorber A/B preheater gas temperature | <datalog>
20 | TC11 | ADS_PH_ROD_TEM_RD_ | Adsorber A/B preheater wall temperature | <datalog>
21 | TC12 | ADS_C_BED_TEM_RD_ | Adsorber C vessel bed temperature | <datalog>
22 | TC13 | ADS_C_WALL_TEM_RD_ | Adsorber C vessel wall temperature | <datalog>
23 | TC14 | ADS_D_BED_TEM_RD_ | Adsorber D vessel bed temperature | <datalog>
24 | TC15 | ADS_D_WALL_TEM_RD_ | Adsorber D vessel wall temperature | <datalog>
25 | REGEN_HRS_LEFT | RG_HRS_LEFT_ | Hours remaining in current regen step
26 | REGEN_MIN_LEFT | RG_MIN_LEFT_ | Minutes remaining in current regen step
27
28 | PREHEATER_SP | PREHEATER_SP_ | Adsorber Preheater Setpoint | <datalog> ADS Preheater PID Setpoint
29 | ADS_PH_PID_DATA.CVP | ADS_PH_PID_DT_CVP | Ads Preheater Dutycycle Output | PID ADS Preheater
30 | BLANKET_SP | BLANKET_SP_ | Adsorber Blanket Setpoint | <datalog> ADS Blanket PID Setpoint
31 | ADS_A_BLKT_PID_DATA.CVP | ADS_A_BKT_PID_DT_CVP | Adsorber A Blanket Dutycycle Output | PID ADS A Blanket
32 | ADS_B_BLKT_PID_DATA.CVP | ADS_B_BKT_PID_DT_CVP | Adsorber B Blanket Dutycycle Output | PID ADS B Blanket
33 | ADS_C_BLKT_PID_DATA.CVP | ADS_C_BKT_PID_DT_CVP | Adsorber C Blanket Dutycycle Output
34 | ADS_D_BLKT_PID_DATA.CVP | ADS_D_BKT_PID_DT_CVP | Adsorber D Blanket Dutycycle Output
35 36 | TOTAL_FLOW | TOTAL_FLOW_ | Total accumulated feedgas flow (32-bit value)
37 | HOURS_LEFT_IN_PURIFY | HR_LEFT_IN_PUR_ | Hours remaining in purify
38 | MIN_LEFT_IN_PURIFY | MIN_LEFT_IN_PUR_ | Minutes remaining in purify
39 | H2_SENSOR_LEVEL | H2_SNSR_LEVEL_ | Hydrogen level sensor
1440 | MB_HEARTBEAT_ON | MB_HB_ON_EN | Communications heartbeat
1441 | SYSTEM_ALARM_FLAG | SYSTEM_ALM_FLAG_ | Alarm has stopped the system
1442 | REGEN_ALARM_FLAG | RG_ALM_FLAG_ | Alarm has interrupted the regen process
1443 | PURIFY_ALARM_FLAG |  | Alarm has interrupted the purify process
1444 | WARNING |  | SYSTEM, REGEN, or PURIFY Warning
1445 | SYSTEM_STANDBY | SYSTEM_STANDBY_ | System is in standby | STATE System Standby
1446 | PURIFY_MANUAL_HOLD | PUR_MANUAL_HOLD_ | Manual purify hold command | STATE Purify Manual Hold
1447 | SET_REGEN_HOLD | SET_RG_HOLD_ | Manual regen hold command
1448 | EMO_ACTIVE | EMO_ACT_ | Emergency stop has been pressed | STATUS The EMO has been depressed
1449 | PROC_REGEN_A | PROC_RG_A_ | Bed A is in Regen | STATE Process Regen A
1450 | PROC_REGEN_B | PROC_RG_B_ | Bed B is in Regen | STATE Process Regen B
1451 | PROC_REGEN_C | PROC_RG_C_ | Bed C is in Regen | STATE Process Regen C
1452 | PROC_REGEN_D | PROC_RG_D_ | Bed D is in Regen | STATE Process Regen D
1454 | ALARM_RELAY_CONFIG | ALM_RLY_CONFIG_ | Alarm Relay configuration (0 = standard, 1 = failsafe)
1456 | ADS_A_REGEN_IN_OUT | ADS_A_RG_IN_OUT_ | AV1/AV6 OPEN - Adsorber A regeneration gas outlet/inlet valve | SV-1
1457 | ADS_A_PURIFY_OPEN | ADS_A_PUR_OPEN_ | AV2/AV7 OPEN - Adsorber A process gas inlet/outlet valve | SV-2
1458 | ADS_B_PURIFY_OPEN | ADS_B_PUR_OPEN_ | AV3/AV8 OPEN - Adsorber B process gas inlet/outlet valve | SV-3
1459 | ADS_B_REGEN_IN_OUT | ADS_B_RG_IN_OUT_ | AV4/AV9 OPEN - Adsorber B regeneration gas outlet/inlet valve | SV-4
1460 | BYPASS_VALVE | BYPASS_VLV_ | SV-5 Bypass (AUTO: closed, PMAN: open) | SV-5
1461 | H2_INLET_VALVE | H2_INLET_VLV_ | AV-10 OPEN - H2 Mixing Panel Valve | SV-6 Hydrogen mixing panel inlet valve
1462 | PROC_GAS_INLET_VALVE | PROC_GAS_INLET_VLV_ | AV-11 OPEN - Process Gas Mixing Panel Valve | SV-7 Process gas mixing panel inlet valve
1463 | EQUALIZE_VALVE_AB | EQL_VLV_AB_ | AV-20 OPEN - Equalize valve | SV-8A
1464 | ADS_A_PURIFY_CLOSE | ADS_A_PUR_CLOSE_ | AV2/AV7 CLOSE - Adsorber A process gas inlet/outlet valve | SV-2B
1465 | ADS_B_PURIFY_CLOSE | ADS_B_PUR_CLOSE_ | AV3/AV8 CLOSE - Adsorber B process gas inlet/outlet valve | SV-3B
1466 | ADS_C_REGEN_IN_OUT | ADS_C_RG_IN_OUT_ | AV-12/AV-14 OPEN - Adsorber C regeneration gas outlet/inlet valve | SV-9A
1467 | ADS_C_PURIFY_OPEN | ADS_C_PUR_OPEN_ | AV-13/AV-15 OPEN - Adsorber C process gas inlet/outlet valve | SV-10A
1468 | ALARM_BUZZER_OUT | ALM_BUZZER_OUT_ | Buzzer output alarm | ALARM Buzzer Output
1469 | WATCHDOG | WATCHDOG_ | Watchdog relay | K7
1470 | ALARM_RELAY | ALM_RLY_ | Alarm/warning relay configuration (1=failsafe, 0=standard) | K8
1471 | GAS_RELAY | GAS_RLY_ | Gas relay | K9
1472 | EQUALIZE_VALVE_CD | EQL_VLV_CD_ | AV-21 OPEN - Equalize valve | SV-11A
1473 | ADS_C_PURIFY_CLOSE | ADS_C_PUR_CLOSE_ | AV-13/AV-15 CLOSE - Adsorber C process gas inlet/outlet valve | SV-10B
1474 | ADS_D_REGEN_IN_OUT | ADS_D_RG_IN_OUT_ | AV-16/AV-18 OPEN - Adsorber D regeneration gas inlet/outlet valve | SV-12A
1475 | ADS_D_PURIFY_OPEN | ADS_D_PUR_OPEN_ | AV-17/AV-19 OPEN - Adsorber D process gas inlet/outlet valve | SV-13A
1477 | ADS_D_PURIFY_CLOSE | ADS_D_PUR_CLOSE_ | AV-17/AV-19 CLOSE - Adsorber D process gas inlet/outlet valve | SV-13B
1488 | ADS_PH_CONTACTOR | ADS_PH_CTR_ | Preheater Power | K1/K12
1489 | ADS_A_BLKT_CONTACTOR | ADS_A_BKT_CTR_ | Vessel A Heater Power | K2
1490 | ADS_B_BLKT_CONTACTOR | ADS_B_BKT_CTR_ | Vessel B Heater Power | K3
1491 | ADS_C_BLKT_CONTACTOR | ADS_C_BKT_CTR_ | Vessel C Heater Power | K4
1492 | ADS_D_BLKT_CONTACTOR | ADS_D_BKT_CTR_ | Vessel D Heater Power | K5
1494 | ADS_PREHEATER_SSR | ADS_PREHEATER_SSR_ | SSR1 - Preheater Rod Heating Control | SSR1
1495 | ADS_BLANKET_SSR | ADS_BLANKET_SSR_ | SSR2 - Blanket Heating Control | SSR2
1504 | EXOTHERM_ALARM | EXOTHERM_ALM_ | Purify High Temp alarm
1505 | PLC_FAULT_ALARM | PLC_FAULT_ALM_ | Major PLC Fault alarm
1506 | UPS_FAULTED_ALARM | UPS_FAULTED_ALM_ | Uninterrupted Power Supply failure alarm | ALARM UPS Fail
1513 | LOW_PLC_BATTERY_ALM | LOW_PLC_BATT_ALM_ | Low PLC Battery alarm | ALARM Low PLC Battery
1514 | GFI_TRIPPED_ALARM | GFI_TRIPPED_ALM_ | GFI Tripped alarm | ALARM GFI Tripped
1515 | MAIN_PWR_ALARM | MAIN_PWR_ALM_ | Main Power Fail alarm | ALARM Main Power Fail
1516 | CTL_PWR_ALARM | CTL_PWR_ALM_ | Control Power Fail alarm | ALARM Control Power Fail
1517 | LP_OUT_GAS_ALARM | LP_OUT_GAS_ALM_ | Gas Low Outlet Pressure alarm
1518 | LP_INLET_GAS_ALARM | LP_INLET_GAS_ALM_ | Gas Low Inlet Pressure alarm | ALARM Low Gas Pressure
1519 | HP_INLET_GAS_ALARM | HP_INLET_GAS_ALM_ | Gas Inlet High Pressure alarm | ALARM Gas Inlet High Pressure
1520 | HP_OUT_GAS_ALARM | HP_OUT_GAS_ALM_ | Gas Outlet High pressure alarm | ALARM Gas Outlet High Pressure
1521 | OPEN_PX1_ALARM | OPEN_PX1_ALM_ | Gas Inlet PX open alarm | ALARM Gas Inlet Pressure Transmitter Broken
1522 | OPEN_PX2_ALARM | OPEN_PX2_ALM_ | Gas Outlet PX open alarm | ALARM Gas Outlet Pressure Transmitter Broken
1524 | SAFETY_VENT_ALARM | SAFETY_VENT_ALM_ | Overpressure Event alarm
1536 | PURIFY_HOLD_ALARM | PUR_HOLD_ALM_ | System Purify Hold alarm | ALARM Purify Hold
1537 | LT_INLET_GAS_ALARM | LT_INLET_GAS_ALM_ | Inlet Low Temperature alarm | ALARM Inlet Gas Low Temp Alarm
1552 | HTI_ALARM | HTI_ALM_ | High Temp Interlock alarm | ALARM High Temperature Interlocks
1553 | PH_FAULT_ALARM | PH_FAULT_ALM_ | Preheater Failed to Heat alarm | ALARM Preheater Fault
1554 | H2_LEVEL_ALARM | H2_LEVEL_ALM_ | Hydrogen level alarm
1555 | OPEN_PX_3_ALARM | OPEN_PX3_ALM_ | Blend Station Open PX alarm
1556 | LP_BLEND_GAS_ALARM | LP_BLEND_GAS_ALM_ | Low Pressure Blend Gas alarm
1557 | HP_BLEND_GAS_ALARM | HP_BLEND_GAS_ALM_ | High Pressure Blend Gas alarm
1558 | BLEND_GAS_LEAK_ALARM | BLEND_GAS_LEAK_ALM_ | Blend Gas Leak Detected alarm
1559 | LOW_REG_PW_DEV_ALARM | LOW_REG_PW_DEV_ALM_ | Regen Low Power Deviation alarm
1560 | HI_REG_PW_DEV_ALARM | HI_REG_PW_DEV_ALM_ | Regen High Power Deviation alarm
1561 | LP_EXT_PNEU_ALARM | LP_EXT_PNEU_ALM_ | Low External Pneumatic Pressure alarm | ALARM System Pneumatic Pressure Low
1562 | LP_INT_PNEU_ALARM | LP_INT_PNEU_ALM_ | Low Internal Pneumatic Pressure alarm
1563 | REG_COOL_FAIL_ALARM | REG_COOL_FAIL_ALM_ | Regen Cooling Failure alarm
1564 | OPEN_TC10_ALARM | OPEN_TC10_ALM_ | Open TC10 on Preheater Gas alarm
1565 | OPEN_TC11_ALARM | OPEN_TC11_ALM_ | Open TC11 on Preheater Rod alarm
1566 | HT_PH_GAS_ALARM | HT_PH_GAS_ALM_ | High Temp Preheater Gas alarm
1567 | HT_PH_ROD_ALARM | HT_PH_ROD_ALM_ | High Temp Preheater Rod alarm
1569 | OPEN_TC6_ALARM | OPEN_TC6_ALM_ | Adsorber A Bed TC6 Open alarm | ALARM Adsorber A Bed Thermocouple Open
1571 | OPEN_TC7_ALARM | OPEN_TC7_ALM_ | Adsorber A Wall TC7 Open alarm | ALARM Adsorber A Wall Thermocouple Open
1573 | HT_WALL_ADS_A_ALARM | HT_WALL_ADS_A_ALM_ | Adsorber A Regen Wall High Temp alarm | ALARM ADS A REGEN Wall High Temp
1574 | LT_BED_ADS_A_ALARM | LT_BED_ADS_A_ALM_ | Adsorber A Bed Low Temp alarm | ALARM ADS A Wall Low Temperature
1575 | ADS_A_EXOTHERM_ALARM | ADS_A_EXOTHERM_ALM_ | Adsorber A Purify High Temp alarm | ALARM ADS A Purify High Temp
1576 | HT_BED_ADS_A_ALARM | HT_BED_ADS_A_ALM_ | Adsorber A Bed High Temp alarm
1585 | OPEN_TC8_ALARM | OPEN_TC8_ALM_ | Adsorber B Bed TC8 Open alarm | ALARM Adsorber B Bed Thermocouple Open
1587 | OPEN_TC9_ALARM | OPEN_TC9_ALM_ | Adsorber B Wall TC9 Open alarm | ALARM Adsorber B Wall Thermocouple Open
1589 | HT_WALL_ADS_B_ALARM | HT_WALL_ADS_B_ALM_ | Adsorber B Regen Wall High Temp alarm | ALARM ADS B REGEN Wall High Temp
1590 | LT_BED_ADS_B_ALARM | LT_BED_ADS_B_ALM_ | Adsorber B Bed Low Temp alarm | ALARM ADS B Wall Low Temperature
1591 | ADS_B_EXOTHERM_ALARM | ADS_B_EXOTHERM_ALM_ | Adsorber B Purify High Temp alarm | ALARM ADS B Purify High Temp
1592 | HT_BED_ADS_B_ALARM | HT_BED_ADS_B_ALM_ | Adsorber B Bed High Temp alarm
1601 | OPEN_TC12_ALARM | OPEN_TC12_ALM_ | Adsorber C Bed TC12 Open alarm
1603 | OPEN_TC13_ALARM | OPEN_TC13_ALM_ | Adsorber C Wall TC13 Open alarm
1605 | HT_WALL_ADS_C_ALARM | HT_WALL_ADS_C_ALM_ | Adsorber C Regen Wall High Temp alarm
1606 | LT_BED_ADS_C_ALARM | LT_BED_ADS_C_ALM_ | Adsorber C Bed Low Temp alarm
1607 | ADS_C_EXOTHERM_ALARM | ADS_C_EXOTHERM_ALM_ | Adsorber C Purify High Temp alarm
1608 | HT_BED_ADS_C_ALARM | HT_BED_ADS_C_ALM_ | Adsorber C Bed High Temp alarm
1617 | OPEN_TC14_ALARM | OPEN_TC14_ALM_ | Adsorber D Bed TC14 Open alarm
1619 | OPEN_TC15_ALARM | OPEN_TC15_ALM_ | Adsorber D Wall TC15 Open alarm
1621 | HT_WALL_ADS_D_ALARM | HT_WALL_ADS_D_ALM_ | Adsorber D Regen Wall High Temp alarm
1622 | LT_BED_ADS_D_ALARM | LT_BED_ADS_D_ALM_ | Adsorber D Bed Low Temp alarm
1623 | ADS_D_EXOTHERM_ALARM | ADS_D_EXOTHERM_ALM_ | Adsorber D Purify High Temp alarm
1624 | HT_BED_ADS_D_ALARM | HT_BED_ADS_D_ALM_ | Adsorber D Bed High Temp alarm
1632 | SCREEN_COMMS_ERROR | SCREEN_COMMS_ERR_ | Communication error between HMI and PLC warning
1634 | UPS_FAULTED_WARN | UPS_FAULTED_WRN_ | Uninterrupted Power Supply failure warning | WARNING UPS Fail
1641 | LOW_PLC_BATTERY_WARN | LOW_PLC_BATT_WRN_ | Low PLC Battery warning | WARNING Low PLC Battery
1642 | GFI_TRIPPED_WARN | GFI_TRIPPED_WRN_ | GFI Tripped warning | WARNING GFI Tripped
1643 | MAIN_PWR_WARN | MAIN_PWR_WRN_ | Main Power Fail warning | WARNING Control Power Fail
1644 | CTL_PWR_WARN | CTL_PWR_WRN_ | Control Power Fail warning | WARNING Control Power Fail
1645 | LP_OUT_GAS_WARN | LP_OUT_GAS_WRN_ | Gas Outlet Low Pressure warning
1646 | LP_INLET_GAS_WARN | LP_INLET_GAS_WRN_ | Gas Inlet Low Pressure warning | WARNING Low Gas Pressure
1647 | HP_INLET_GAS_WARN | HP_INLET_GAS_WRN_ | Gas Inlet High Pressure warning | WARNING Gas Inlet High Pressure
1648 | HP_OUT_GAS_WARN | HP_OUT_GAS_WRN_ | Gas Outlet High Pressure warning | WARNING Gas Outlet High Pressure
1649 | OPEN_PX1_WARN | OPEN_PX1_WRN_ | Gas Inlet PX open warning | WARNING Gas Inlet Pressure Transmitter Broken
1650 | OPEN_PX2_WARN | OPEN_PX2_WRN_ | Gas Outlet PX open warning | WARNING Gas Outlet Pressure Transmitter Broken
1652 | SAFETY_VENT_WARN | SAFETY_VENT_WRN_ | Overpressure Event warning
1661 | MODBUS_ERROR | MODBUS_ERR_ | Loss of communication to Modbus
1664 | PURIFY_HOLD_WARN | PUR_HOLD_WRN_ | System Purify Hold warning | WARNING System Purify Hold
1665 | LT_INLET_GAS_WARN | LT_INLET_GAS_WRN_ | Inlet Low Temperature warning | ALARM Inlet Gas Low Temp Warning
1680 | HTI_WARN | HTI_WRN_ | High Temp Interlock warning | WARNING High Temperature Interlocks
1681 | PH_FAULT_WARN | PH_FAULT_WRN_ | Preheater Failed to Heat warning | WARNING Preheater Fault
1682 | H2_LEVEL_WARN | H2_LEVEL_WRN_ | High hydrogen level warning
1683 | OPEN_PX3_WARN | OPEN_PX3_WRN_ | Blend Station Open PX warning
1684 | LP_BLEND_GAS_WARN | LP_BLEND_GAS_WRN_ | Low Pressure Blend Gas warning
1685 | HP_BLEND_GAS_WARN | HP_BLEND_GAS_WRN_ | High Pressure Blend Gas warning
1686 | BLEND_GAS_LEAK_WARN | BLEND_GAS_LEAK_WRN_ | Blend Gas Leak Detected warning
1687 | LOW_REG_PW_DEV_WARN | LOW_REG_PW_DEV_WRN_ | Regen Low Power Deviation warning
1688 | HI_REG_PW_DEV_WARN | HI_REG_PW_DEV_WRN_ | Regen High Power Deviation warning
1689 | LP_EXT_PNEU_WARN | LP_EXT_PNEU_WRN_ | Low External Pneumatic Pressure warning | WARNING System Pneumatic Pressure Low
1690 | LP_INT_PNEU_WARN | LP_INT_PNEU_WRN_ | Low Internal Pneumatic Pressure warning
1691 | REG_COOL_FAIL_WARN | REG_COOL_FAIL_WRN_ | Regen Cooling Failure warning
1692 | OPEN_TC10_WARN | OPEN_TC10_WRN_ | Open TC10 on Preheater Gas warning
1693 | OPEN_TC11_WARN | OPEN_TC11_WRN_ | Open TC11 on Preheater Rod warning
1694 | HT_PH_GAS_WARN | HT_PH_GAS_WRN_ | High Temp Preheater Gas warning
1695 | HT_PH_ROD_WARN | HT_PH_ROD_WRN_ | High Temp Preheater Rod warning
1697 | OPEN_TC6_WARN | OPEN_TC6_WRN_ | Adsorber A Bed TC6 Open warning | WARNING Adsorber A Bed Thermocouple Open
1699 | OPEN_TC7_WARN | OPEN_TC7_WRN_ | Adsorber A Wall TC7 Open warning | WARNING Adsorber A Wall Thermocouple Open
1701 | HT_WALL_ADS_A_WARN | HT_WALL_ADS_A_WRN_ | Adsorber A Regen Wall High Temp warning | WARNING ADS A Wall High Temperature
1702 | LT_BED_ADS_A_WARN | LT_BED_ADS_A_WRN_ | Adsorber A Bed Low Temp warning | WARNING ADS A Wall Low Temperature
1703 | ADS_A_EXOTHERM_WARN | ADS_A_EXOTHERM_WRN_ | Adsorber A Purify High Temp warning | WARNING ADS A Purify High Temp
1704 | HT_BED_ADS_A_WARN | HT_BED_ADS_A_WRN_ | Adsorber A Bed High Temp warning
1713 | OPEN_TC8_WARN | OPEN_TC8_WRN_ | Adsorber B Bed TC8 Open warning | WARNING Adsorber B Bed Thermocouple Open
1715 | OPEN_TC9_WARN | OPEN_TC9_WRN_ | Adsorber B Wall TC9 Open warning | WARNING Adsorber B Wall Thermocouple Open
1717 | HT_WALL_ADS_B_WARN | HT_WALL_ADS_B_WRN_ | Adsorber B Regen Wall High Temp warning | WARNING ADS B Wall High Temperature
1718 | LT_BED_ADS_B_WARN | LT_BED_ADS_B_WRN_ | Adsorber B Bed Low Temp warning | WARNING ADS B Wall Low Temperature
1719 | ADS_B_EXOTHERM_WARN | ADS_B_EXOTHERM_WRN_ | Adsorber B Purify High Temp warning | WARNING ADS B Purify High Temp
1720 | HT_BED_ADS_B_WARN | HT_BED_ADS_B_WRN_ | Adsorber B Bed High Temp warning
1729 | OPEN_TC12_WARN | OPEN_TC12_WRN_ | Adsorber C Bed TC12 Open warning
1731 | OPEN_TC13_WARN | OPEN_TC13_WRN_ | Adsorber C Wall TC13 Open warning
1733 | HT_WALL_ADS_C_WARN | HT_WALL_ADS_C_WRN_ | Adsorber C Regen Wall High Temp warning
1734 | LT_BED_ADS_C_WARN | LT_BED_ADS_C_WRN_ | Adsorber C Bed Low Temp warning
1735 | ADS_C_EXOTHERM_WARN | ADS_C_EXOTHERM_WRN_ | Adsorber C Purify High Temp warning
1736 | HT_BED_ADS_C_WARN | HT_BED_ADS_C_WRN_ | Adsorber C Bed High Temp warning
1745 | OPEN_TC14_WARN | OPEN_TC14_WRN_ | Adsorber D Bed TC14 Open warning
1747 | OPEN_TC15_WARN | OPEN_TC15_WRN_ | Adsorber D Wall TC15 Open warning
1749 | HT_WALL_ADS_D_WARN | HT_WALL_ADS_D_WRN_ | Adsorber D Regen Wall High Temp warning
1750 | LT_BED_ADS_D_WARN | LT_BED_ADS_D_WRN_ | Adsorber D Bed Low Temp warning
1751 | ADS_D_EXOTHERM_WARN | ADS_D_EXOTHERM_WRN_ | Adsorber D Purify High Temp warning
1752 | HT_BED_ADS_D_WARN | HT_BED_ADS_D_WRN_ | Adsorber D Bed High Temp warning