## Sheet1
Number | Doc Tag Name | My Tag Name | Doc Description | My description
0 | PURIFY_OVERLAP_SEC | PUR_OVL_SEC_ACC | Current purify overlap time | TIMER Purify Overlap
1 | REGEN_DELAY_TIMER | RG_DELAY_TMR_ACC | Current seconds in current minute of regeneration step | TIMER Regen Delay (seconds)
2 | REGEN_VENT_SEC_TMR | RG_VENT_SEC_TMR_ACC | Current seconds in current minute of vent step | TIMER Regen Vent (seconds)
3 | REGEN_COOL_SEC_TIMER | RG_COOL_SEC_TMR_ACC | Current seconds in current minute of coolstep | TIMER Regen Cool (seconds)
4 | PURIFY_ACTIVE_TTL_HR | PUR_ACT_TTL_HR_ACC | Total hours purifying current purify vessel (reset at 24) | COUNTER The number of total elapsed purification hours for the process equipment
5 | PURIFY_ACTIVE_TTL_DY | PUR_ACT_TTL_DY_ACC | Total days purifying current purify vessel | COUNTER The number of total elapsed purification days for the process equipment
6 | PURIFY_ACTIVE_MINUTE | PUR_ACT_MIN_ACC | Active Purify minutes | COUNTER The number of elapsed purification minutes for the current ADS (60 min)
7 | PURIFY_ACTIVE_HOURS | PUR_ACT_HR_ACC | Active Purify Hours | COUNTER The number of elapsed purification hours for the current ADS
8 | REGEN_VENT_MIN_CTR | RG_VENT_MIN_CTR_ACC | Active minutes in current regen vent step
9 | REGEN_VENT_HRS_CTR | RG_VENT_HRS_CTR_ACC | Active hours in current regen vent step
10 | REGEN_RUN_MINUTE | RG_RUN_MIN_ACC | Active minutes in current regen run step
11 | REGEN_COOL_MINUTE | RG_COOL_MIN_ACC | Active minutes in current regen cool step | COUNTER Regen the number of minutes for which the bed has cooled
12 | REGEN_EQUALIZE_MIN | RG_EQL_MIN_ACC | Active minutes in current regen equalize step
13 | REGEN_COND_MIN_CTR | RG_COND_MIN_CTR_ACC | Active minutes in current regen condition step
14 | REGEN_COND_HRS_CTR | RG_COND_HRS_CTR_ACC | Active hours in current regen condition step
15 | PURIFY_OVERLAP_MIN | PUR_OVL_MIN_ACC | Active minutes in current regen overlap step
16 | MIN_LEFT_IN_PURIFY | MIN_LEFT_IN_PUR_ | Minutes left in current hour of purify mode
17 | HRS_LEFT_IN_PURIFY | HRS_LEFT_IN_PUR_ | Hours left in current day of purify mode
18 | REGEN_MIN_LEFT | RG_MIN_LEFT_ | Minutes left in current hour of regen
19 | REGEN_HRS_LEFT | RG_HRS_LEFT_ | Hours left in current day of regen
20 | REGEN_STATE | RG_STAT_ | Current Regen step | <datalog> The current state of the regen process
21 | MOISTURE_SENSOR_TEMP | MOIST_SNSR_TEM_ | Moisture sensor reading | <datalog> Moisture sensor MS-1 temp C.
22 | MFM_FLOW | MFM_FLOW_ | Mass flow meter reading
23 | INLET_PX_PSIG | INLET_PX_PSIG_ | Inlet pressure | <datalog> Inlet pressure PX_1 in PSIG.
24 | OUTLET_PX_PSIG | OUTLET_PX_PSIG_ | Outlet pressure | <datalog> Outlet pressure PX-2 in PSIG.
25 | ADS_A_BED_TEMP_READ-TC6 | ADS_A_BED_TEM_RD_ | Adsorber A vessel bed temperature | <datalog> Adsorber A bed TC6 bed temp C
26 | ADS_A_WALL_TEMP_READ-TC7 | ADS_A_WALL_TEM_RD_ | Adsorber A vessel wall temperature | <datalog> Adsorber A wall TC7 bed temp C
27 | ADS_B_BED_TEMP_READ-TC8 | ADS_B_BED_TEM_RD_ | Adsorber B vessel bed temperature | <datalog> Adsorber B bed TC8 bed temp C
28 | ADS_B_WALL_TEMP_READ-TC9 | ADS_B_WALL_TEM_RD_ | Adsorber B vessel wall temperature | <datalog> Adsorber B bed TC9 wall temp C
29 | PH_A_GAS_TEMP_READ-TC10 | PH_A_GAS_TEM_RD_ | Adsorber A preheater gas temperature | <datalog> Adsorber A TC10 PH gas temp C
30 | PH_A_ROD_TEMP_READ-TC11 | PH_A_ROD_TEM_RD_ | Adsorber A preheater rod temperature | <datalog>
31 | PH_B_GAS_TEMP_READ-TC12 | PH_B_GAS_TEM_RD_ | Adsorber B preheater gas temperature | <datalog> Adsorber B TC12 PH gas temp C
32 | PH_B_ROD_TEMP_READ-TC13 | PH_B_ROD_TEM_RD_ | Adsorber B preheater rod temperature | <datalog> Adsorber B TC13 PH wall temp C
33 | TOTAL_FLOW-low word | TOTAL_FLOW_ | Low 16 bits of 32-bit integer
34 | TOTAL_FLOW-high word | TOTAL_FLOW_ | High 16 bits of 32-bit integer
35 | ADS_A_BED_TEMP-TC6 | ADS_A_BED_TEM_ | Adsorber A vessel bed temperature raw | Adsorber A TC6 bed temp C
36 | ADS_A_WALL_TEMP-TC7 | ADS_A_WALL_TEM_ | Adsorber A vessel wall temperature raw | Adsorber A TC7 wall temp C
37 | ADS_B_BED_TEMP-TC8 | ADS_B_BED_TEM_ | Adsorber B vessel bed temperature raw | Adsorber B TC8 bed temp C
38 | ADS_B_WALL_TEMP-TC9 | ADS_B_WALL_TEM_ | Adsorber B vessel wall temperature raw | Adsorber B TC9 wall temp C
39 | PREHEATER_SP | PREHEATER_SP_ | Preheater setpoint | <datalog> CONTROL Preheater PID Setpoint
40 | BLANKET_SP | BLANKET_SP_ | Blanket setpoint | CONTROL Blanket PID Setpoint
41 | PROC_STATE | PROC_STAT_ | Process state | STATE The current state of the process
42 | ADS_PH_GAS_TEMP-TC10 | ADS_B_PH_GAS_TEM_ | ADS A or B preheater gas PID process variable | Vessel B TC12 PH gas temp C
43 | ADS_PH_PID_DATA.CVP | ADS_B_PH_PID_DT_CVP | ADS A or B preheater gas PID dutycycle output
44 | ADS_WALL_TEMP | ADS_B_WALL_TEM_ | ADS A or B blanket PID process variable | Adsorber B TC9 wall temp C
45 | ADS_BLKT_PID_DATA.CVP | ADS_B_BKT_PID_DT_CVP | ADS A or B blanket PID dutycycle output | PID ADS B Blanket
1440 | MB_HEARTBEAT_ON | MB_HB_ON_EN | Flashing bit to indicate values are updating
1441 | SYSTEM_ALARM_FLAG | SYSTEM_ALM_FLAG_ | System alarm
1442 | PURIFY_ALARM_FLAG |  | Purify alarm
1443 | REGEN_ALARM_FLAG | RG_ALM_FLAG_ | Regen alarm
1444 | WARNING |  | Warning indicator
1445 | EMO_ACTIVE | EMO_ACT_ | Emergency stop is active (option) | STATUS The EMO has been depressed
1446 | PURIFY_MANUAL_HOLD | PUR_MANUAL_HOLD_ | Manual purify hold | STATE Purify Manual Hold
1447 | SET_REGEN_HOLD | SET_RG_HOLD_ | Manual regen hold
1448 | PROC_PURIFY_A | ADS_A_PUR_OPEN_ | Bed A is purifying | SV2A AV2/AV7 OPEN
1449 | PROC_PURIFY_B | ADS_B_PUR_OPEN_ | Bed B is purifying | SV3A AV3/AV8 OPEN
1452 | ALARM_RELAY_CONFIG | ALM_RLY_CONFIG_ | Alarm/warning relay configuration (1=failsafe, 0=standard)
1453 | SYSTEM_STANDBY | SYSTEM_STANDBY_ | Purifier in standby/offline | STATE System Standby
1454 | REGEN_HEAT_STATUS |  | Regen at operating temperature status
1455 | REGEN_OFFLINE |  | Regen offline
1456 | AV1A/6A OPEN | ADS_A_RG_IN_OUT_ | Adsorber A regeneration gas outlet/inlet valve | SV1A AV1/AV6 OPEN
1457 | AV2A/7A OPEN | ADS_A_PUR_OPEN_ | Adsorber A process gas inlet/outlet valve | SV2A AV2/AV7 OPEN
1458 | AV3A/8A OPEN | ADS_B_PUR_OPEN_ | Adsorber B process gas inlet/outlet valve | SV3A AV3/AV8 OPEN
1459 | AV4A/9A OPEN | ADS_B_RG_IN_OUT_ | Adsorber B regeneration gas outlet/inlet valve | SV4A AV4/AV9 OPEN
1460 | AV5 | BYPASS_VLV_ | Bypass valve | SV-5
1461 | AV20A OPEN | EQL_VLV_AB_ | Bed A-B equalizing valve | SV8A / AV20
1462 | AV2B/7B CLOSE | ADS_A_PUR_CLOSE_ | Adsorber A process gas inlet/outlet valve | SV2B AV2/AV7 CLOSE
1463 | AV3B/8B CLOSE | ADS_B_PUR_CLOSE_ | Adsorber B process gas outlet/inlet valve | SV3B AV3/AV8 CLOSE
1464 | VSL_A_CONTACTORS | VSL_A_CTR_ | K1,2,3 | K1,2,3
1465 | VSL_B_CONTACTORS | VSL_B_CTR_ | K4,5,6 | K4,5,6
1466 | ROD_HEATER_CTRL | ROD_HEATER_CTRL_ | SSR4-7 | SSR4-7
1467 | BLKT_HEATER_CTRL | BKT_HEATER_CTRL_ | SSR1-2 | SSR1-2
1469 | WATCHDOG | WATCHDOG_ | PLC Watchdog | K7
1470 | ALARM_RELAY | ALM_RLY_ | Alarm relay (configurable as failsafe or standard) | K8
1471 | GAS_RELAY | GAS_RLY_ | Gas relay | K9
1504 | HT_PURIFY_ALARM | HT_PUR_ALM_ | High Adsorber temperature during purify alarm
1505 | PLC_FAULT_ALARM | PLC_FAULT_ALM_ | PLC faulted alarm
1506 | UPS_FAULTED_ALARM | UPS_FAULTED_ALM_ | UPS Fault alarm
1513 | LOW_PLC_BATTERY_ALM | LOW_PLC_BATT_ALM_ | PLC battery low alarm | ALARM System Low PLC Battery
1514 | GFI_TRIPPED_ALARM | GFI_TRIPPED_ALM_ | Ground Fault trip alarm | ALARM System GFI Tripped
1515 | MAIN_PWR_ALARM | MAIN_PWR_ALM_ | Main power failed alarm | ALARM System Main Power Fail
1516 | CTL_PWR_ALARM | CTL_PWR_ALM_ | Control power failed alarm | ALARM System Control Power Fail
1517 | LP_INLET_GAS_ALARM | LP_INLET_GAS_ALM_ | Low pressure inlet gas alarm
1518 | LP_OUTLET_GAS_ALARM | LP_OUTLET_GAS_ALM_ | Low pressure outlet gas alarm | ALARM System Low Gas Pressure
1519 | HP_INLET_GAS_ALARM | HP_INLET_GAS_ALM_ | High pressure inlet gas alarm | ALARM Gas Inlet High Pressure
1520 | HP_OUT_GAS_ALARM | HP_OUT_GAS_ALM_ | High pressure outlet gas alarm | ALARM Gas Outlet High Pressure
1521 | OPEN_PX1_ALARM | OPEN_PX1_ALM_ | Inlet pressure transducer open circuit alarm | ALARM Gas Inlet Pressure Transmitter Broken
1522 | OPEN_PX2_ALARM | OPEN_PX2_ALM_ | Outlet pressure transducer open circuit alarm | ALARM Gas Outlet Pressure Transmitter Broken
1524 | SAFETY_VENT_ALARM | SAFETY_VENT_ALM_ | Safety pressure vent alarm
1536 | PURIFY_HOLD_ALARM | PUR_HOLD_ALM_ | Purify hold alarm | ALARM System Purify Hold
1537 | LT_INLET_GAS_ALARM | LT_INLET_GAS_ALM_ | Low temperature inlet gas alarm
1552 | HTI_ALARM | HTI_ALM_ | High temperature interlocks alarm | ALARM High Temperature Interlocks
1553 | PH_A_FAULT_ALARM | PH_A_FAULT_ALM_ | Failure to heat on Adsorber A Preheater alarm | ALARM Preheater Fault
1559 | LOW_REG_PW_DEV_ALARM | LOW_REG_PW_DEV_ALM_ | Low regen power deviation alarm
1560 | HI_REG_PW_DEV_ALARM | HI_REG_PW_DEV_ALM_ | High regen power deviation alarm
1561 | LP_EXT_PNEU_ALARM | LP_EXT_PNEU_ALM_ | Low external pneumatic pressure alarm | ALARM System Pneumatic Pressure Low
1562 | LP_INT_PNEU_ALARM | LP_INT_PNEU_ALM_ | Low internal pneumatic pressure alarm
1563 | REG_COOL_FAIL_ALARM | REG_COOL_FAIL_ALM_ | Adsorber cooling failure alarm
1564 | OPEN_TC10_ALARM | OPEN_TC10_ALM_ | Open TC on Adsorber A Preheater Gas alarm
1565 | OPEN_TC11_ALARM | OPEN_TC11_ALM_ | Open TC on Adsorber A Preheater Wall alarm
1566 | HT_PH_A_GAS_ALARM | HT_PH_A_GAS_ALM_ | High Temperature on Adsorber A Preheater Gas Alarm
1567 | HT_PH_A_ROD_ALARM | HT_PH_A_ROD_ALM_ | High Temperature on Adsorber A Preheater Rod Alarm
1568 | HT_PH_B_GAS_ALARM | HT_PH_B_GAS_ALM_ | High Temperature on Adsorber B Preheater Gas Alarm
1569 | HT_PH_B_ROD_ALARM | HT_PH_B_ROD_ALM_ | High Temperature on Adsorber B Preheater Rod Alarm
1570 | PH_B_FAULT_ALARM | PH_B_FAULT_ALM_ | Failure to heat on Adsorber B Preheater alarm
1571 | OPEN_TC12_ALARM | OPEN_TC12_ALM_ | Open TC on Adsorber B Preheater Gas alarm
1572 | OPEN_TC13_ALARM | OPEN_TC13_ALM_ | Open TC on Adsorber B Preheater Wall alarm
1584 | HT_PURIFY_A_ALARM | HT_PUR_A_ALM_ | High temperature during purify Bed A alarm | ALARM ADS A Purify High Temp
1585 | OPEN_TC6_ALARM | OPEN_TC6_ALM_ | Open TC on Adsorber A vessel Bed alarm | ALARM Adsorber A Bed Thermocouple Open
1586 | OPEN_TC7_ALARM | OPEN_TC7_ALM_ | Open TC on Adsorber A vessel Wall alarm | ALARM Adsorber A Wall Thermocouple Open
1587 | LT_BED_ADS_A_ALARM | LT_BED_ADS_A_ALM_ | Low temperature on Adsorber A vessel Bed alarm | ALARM ADS A Wall Low Temperature
1588 | HT_BED_ADS_A_ALARM | HT_BED_ADS_A_ALM_ | High temperature on Adsorber A vessel Bed alarm
1589 | HT_WALL_ADS_A_ALARM | HT_WALL_ADS_A_ALM_ | High temperature on Adsorber A vessel Wall alarm | ALARM ADS A REGEN Wall High Temp
1600 | HT_PURIFY_B_ALARM | HT_PUR_B_ALM_ | High temperature during purify Bed B alarm | ALARM ADS B Purify High Temp
1601 | OPEN_TC8_ALARM | OPEN_TC8_ALM_ | Open TC on Adsorber B vessel Bed alarm | ALARM Adsorber B Bed Thermocouple Open
1602 | OPEN_TC9_ALARM | OPEN_TC9_ALM_ | Open TC on Adsorber B vessel Wall alarm | ALARM Adsorber B Wall Thermocouple Open
1603 | LT_BED_ADS_B_ALARM | LT_BED_ADS_B_ALM_ | Low temperature on Adsorber B vessel Bed alarm | ALARM ADS B Wall Low Temperature
1604 | HT_BED_ADS_B_ALARM | HT_BED_ADS_B_ALM_ | High temperature on Adsorber B vessel Bed alarm
1605 | HT_WALL_ADS_B_ALARM | HT_WALL_ADS_B_ALM_ | High temperature on Adsorber B vessel Wall alarm | ALARM ADS B REGEN Wall High Temp
1664 | SCREEN_COMMS_ERROR | SCREEN_COMMS_ERR_ | Screen communications error, warning
1665 | MODBUS_ERROR | MODBUS_ERR_ | Modbus communications error, warning
1666 | UPS_FAULTED_WARN | UPS_FAULTED_WRN_ | UPS Fault Warning
1673 | LOW_PLC_BATTERY_WARN | LOW_PLC_BATT_WRN_ | Low PLC Battery Warning | WARNING System Low PLC Battery
1674 | GFI_TRIPPED_WARN | GFI_TRIPPED_WRN_ | GFI Tripped Warning | WARNING System GFI Tripped
1675 | MAIN_PWR_WARN | MAIN_PWR_WRN_ | Main Power Failure Warning | WARNING System Control Power Fail
1676 | CTL_PWR_WARN | CTL_PWR_WRN_ | Control Power Failure Warning | WARNING System Control Power Fail
1677 | LP_INLET_GAS_WARN | LP_INLET_GAS_WRN_ | Low pressure inlet gas warning
1678 | LP_OUTLET_GAS_WARN | LP_OUTLET_GAS_WRN_ | Low pressure outlet gas warning | WARNING System Low Gas Pressure
1679 | HP_INLET_GAS_WARN | HP_INLET_GAS_WRN_ | High pressure inlet gas warning | WARNING Gas Inlet High Pressure
1680 | HP_OUT_GAS_WARN | HP_OUT_GAS_WRN_ | High pressure outlet gas warning | WARNING Gas Outlet High Pressure
1681 | OPEN_PX1_WARN | OPEN_PX1_WRN_ | Inlet pressure transducer open circuit warning | WARNING Gas Inlet Pressure Transmitter Broken
1682 | OPEN_PX2_WARN | OPEN_PX2_WRN_ | Outlet pressure transducer open circuit warning | WARNING Gas Outlet Pressure Transmitter Broken
1684 | SAFETY_VENT_WARN | SAFETY_VENT_WRN_ | Safety pressure vent warning
1696 | PURIFY_HOLD_WARNING | PUR_HOLD_WRN_ | Purify hold warning | WARNING System Purify Hold
1697 | LT_INLET_GAS_WARN | LT_INLET_GAS_WRN_ | Low temperature inlet gas warning
1712 | HTI_WARN | HTI_WRN_ | High temperature interlocks warning | WARNING High Temperature Interlocks
1713 | PH_A_FAULT_WARN | PH_A_FAULT_WRN_ | Failure to heat on Adsorber A Preheater warning | WARNING Preheater Fault
1719 | LOW_REG_PW_DEV_WARN | LOW_REG_PW_DEV_WRN_ | Low regen power deviation warning
1720 | HI_REG_PW_DEV_WARN | HI_REG_PW_DEV_WRN_ | High regen power deviation warning
1721 | LP_EXT_PNEU_WARN | LP_EXT_PNEU_WRN_ | Low external pneumatic pressure warning | WARNING System Pneumatic Pressure Low
1722 | LP_INT_PNEU_WARN | LP_INT_PNEU_WRN_ | Low internal pneumatic pressure warning
1723 | REG_COOL_FAIL_WARN | REG_COOL_FAIL_WRN_ | Adsorber cooling failure warning
1724 | OPEN_TC10_WARN | OPEN_TC10_WRN_ | Open TC on Adsorber A Preheater Gas warning
1725 | OPEN_TC11_WARN | OPEN_TC11_WRN_ | Open TC on Adsorber A Preheater Wall warning
1726 | HT_PH_A_GAS_WARN | HT_PH_A_GAS_WRN_ | High Temperature on Adsorber A Preheater Gas warning
1727 | HT_PH_A_ROD_WARN | HT_PH_A_ROD_WRN_ | High Temperature on Adsorber A Preheater Rod warning
1728 | HT_PH_B_GAS_WARN | HT_PH_B_GAS_WRN_ | High Temperature on Adsorber B Preheater Gas warning
1729 | HT_PH_B_ROD_WARN | HT_PH_B_ROD_WRN_ | High Temperature on Adsorber B Preheater Rod warning
1730 | PH_B_FAULT_WARN | PH_B_FAULT_ALM_ | Failure to heat on Adsorber B Preheater warning
1731 | OPEN_TC12_WARN | OPEN_TC12_WRN_ | Open TC on Adsorber B Preheater Gas Warning
1732 | OPEN_TC13_WARN | OPEN_TC13_WRN_ | Open TC on Adsorber B Preheater Wall Warning
1744 | HT_PURIFY_A_WARN | HT_PUR_A_WRN_ | High temperature during purify Bed A warning | WARNING ADS A Purify High Temp
1745 | OPEN_TC6_WARN | OPEN_TC6_WRN_ | Open TC on Adsorber A vessel Bed warning | WARNING Adsorber A Bed Thermocouple Open
1746 | OPEN_TC7_WARN | OPEN_TC7_WRN_ | Open TC on Adsorber A vessel Wall warning | WARNING Adsorber A Wall Thermocouple Open
1747 | LT_BED_ADS_A_WARN | LT_BED_ADS_A_WRN_ | Low temperature on Adsorber A vessel Bed warning | WARNING ADS A Wall Low Temperature
1748 | HT_BED_ADS_A_WARN | HT_BED_ADS_A_WRN_ | High temperature on Adsorber A vessel Bed warning
1749 | HT_WALL_ADS_A_WARN | HT_WALL_ADS_A_WRN_ | High temperature on Adsorber A vessel Wall warning | WARNING ADS A Wall High Temperature
1760 | HT_PURIFY_B_WARN | HT_PUR_B_WRN_ | High temperature during purify Bed B warning | WARNING ADS B Purify High Temp
1761 | OPEN_TC8_WARN | OPEN_TC8_WRN_ | Open TC on Adsorber B vessel Bed warning | WARNING Adsorber B Bed Thermocouple Open
1762 | OPEN_TC9_WARN | OPEN_TC9_WRN_ | Open TC on Adsorber B vessel Wall warning | WARNING Adsorber B Wall Thermocouple Open
1763 | LT_BED_ADS_B_WARN | LT_BED_ADS_B_WRN_ | Low temperature on Adsorber B vessel Bed warning | WARNING ADS B Wall Low Temperature
1764 | HT_BED_ADS_B_WARN | HT_BED_ADS_B_WRN_ | High temperature on Adsorber B vessel Bed warning
1765 | HT_WALL_ADS_B_WARN | HT_WALL_ADS_B_WRN_ | High temperature on Adsorber B vessel Wall warning | WARNING ADS B Wall High Temperature