## Sheet1
Number | Doc Tag Name | My Tag Name | Doc Description | My description
0 | PURIFY_ACTIVE_TTL_DY.ACC | PUR_ACT_TTL_DY_ACC | Count of total days in purification | COUNTER The number of total elapsed purification days for the process equipment
1 | PURIFY_ACTIVE_TTL_HR.ACC | PUR_ACT_TTL_HR_ACC | Count of total purify hours (reset at 24) | COUNTER The number of total elapsed purification hours for the process equipment
2 | PURIFY_ACTIVE_MINUTE.ACC | PUR_ACT_MIN_ACC | Count of current purifying minutes | COUNTER The number of elapsed purification minutes for the current ADS (60 min)
3 | PURIFY_ACTIVE_HOURS.ACC | PUR_ACT_HR_ACC | Count of current purifying hours | COUNTER The number of elapsed purification hours for the current ADS
4 | MIN_LEFT_IN_PURIFY | MIN_LEFT_IN_PUR_ | Minutes left in current hour of purify mode
5 | HRS_LEFT_IN_PURIFY | HRS_LEFT_IN_PUR_ | Hours left in purify mode
6 | GETTER_SERVICE_DAYS.ACC | GETTER_SVC_DAYS_ACC | Count of current getter service days
7 | REGEN_RUN_MINUTE.ACC | RG_RUN_MIN_ACC | Count of current regen minutes
8 | REGEN_COOL_MINUTE.ACC | RG_COOL_MIN_ACC | Count of current regen cool minutes | COUNTER Regen the number of minutes for which the bed has cooled
9 | REGEN_MIN_LEFT | RG_MIN_LEFT_ | Minutes left in current hour of regen | STATUS Preheater Alarm Measured temperature change
10 | REGEN_HRS_LEFT | RG_HRS_LEFT_ | Hour left in regen mode | STATUS Regen Preheater Temperature Initial Temperature
11 | PURIFY_OVERLAP_TIMER.ACC | PUR_OVL_TMR_ACC | Count of seconds in purify overlap | TIMER Purify Overlap
12 | START_PURGE_CTR.ACC | START_PURG_CTR_ACC | Count of vent and backfill loop in startup
13 | H2_LEAK_RST_MIN.ACC | H2_LEAK_RST_MIN_ACC | Minutes left in H2 leak alarm disable reset time
14 | H2_LEAK_RST_SEC.ACC | H2_LEAK_RST_SEC_ACC | Seconds left in current minute of above
15 | START_STATE | START_STAT_ | Start sequence step number
16 | REGEN_STATE | RG_STAT_ | Normal sequence step number | STATE The current state of the regen process
17 | PURGE_STATE | PURG_STAT_ | Cycle purge sequence step number
18 | ADS_A_INLET_PX_PSIG | ADS_A_INLET_PX_PSIG_ | Adsorber A inlet gas pressure reading for display
19 | ADS_B_INLET_PX_PSIG | ADS_B_INLET_PX_PSIG_ | Adsorber B inlet gas pressure reading for display
20 | OUTLET_PX_PSIG | OUTLET_PX_PSIG_ | Outlet gas pressure reading for display
21 | INLET_PX_PSIG | INLET_PX_PSIG_ | Inlet gas pressure reading for display
22 | MFM_CUM_HR | MFM_CUM_HR_ | Mass flow meter reading in cuM/hr
23 | MFC_SLPM | MFC_SLPM_ | Regen mass flow controller
24 | MFC_SETPOINT | MFC_SETPOINT_ | Conversion of set point for screen reading
25 | TC1 | G_1_PH_INNER_TEM_ | Getter C1 preheater inner rod heater temperature | <datalog>
26 | TC2 | G_1_PH_OUTER_TEM_ | Getter C1 preheater outer rod heater temperature | <datalog>
27 | TC3 | G_1_PH_GAS_TEM_ | Getter C1 preheater gas temperature | <datalog>
28 | TC4 | G_1_VSL_WALL_TEM_ | Getter C1 vessel wall temperature | <datalog>
29 | TC5 | G_1_VSL_BED_TEM_ | Getter C1 bed temperature | <datalog>
30 | TC6 | G_2_PH_INNER_TEM_ | Getter C2 preheater inner rod heater temperature | <datalog>
31 | TC7 | G_2_PH_OUTER_TEM_ | Getter C2 preheater outer rod heater temperature | <datalog>
32 | TC8 | G_2_PH_GAS_TEM_ | Getter C2 preheater gas temperature | <datalog>
33 | TC9 | G_2_VSL_WALL_TEM_ | Getter C2 wall temperature | <datalog>
34 | TC10 | G_2_VSL_BED_TEM_ | Getter C2 bed temperature | <datalog>
35 | TC11 | G_3_PH_INNER_TEM_ | Getter C3 preheater inner rod heater temperature | <datalog>
36 | TC12 | G_3_PH_OUTER_TEM_ | Getter C3 preheater outer rod heater temperature | <datalog>
37 | TC13 | G_3_PH_GAS_TEM_ | Getter C3 preheater gas temperature | <datalog>
38 | TC14 | G_3_VSL_WALL_TEM_ | Getter C3 wall temperature | <datalog>
39 | TC15 | G_3_VSL_BED_TEM_ | Getter C3 bed temperature | <datalog>
40 | TC16 | G_VSL_OUT_GAS_TEM_ | Getter outlet gas temperature
41 | TC17 | ADS_PH_GAS_TEM_RD_ | Adsorbers preheater gas heater temperature | <datalog>
42 | TC18 | ADS_PH_ROD_TEM_RD_ | Adsorbers preheater rod temperature | <datalog>
43 | TC19 | ADS_A_WALL_TEM_RD_ | Adsorber A vessel wall temperature | <datalog>
44 | TC20 | ADS_A_BED_TEM_RD_ | Adsorber A bed temperature | <datalog>
45 | TC21 | ADS_B_WALL_TEM_RD_ | Adorber B vessel wall temperature | <datalog>
46 | TC22 | ADS_B_BED_TEM_RD_ | Adsorber B bed temperature | <datalog>
47 | TOTAL_FLOW |  | Total flow (Low word of 32-bit value)
48 | TOTAL_FLOW |  | Total flow (High word of 32-bit value)
49 | GET_1_PH_PID_DATA.SPS | G_1_PH_PID_DT_SPS | Getter C1 preheater setpoint
50 | GET_1_PH_PID_DATA.PV | G_1_PH_GAS_TEM_ | Getter C1 preheater process variable | <datalog>
51 | GET_1_PH_PID_DATA.CVP | G_1_PH_SS_OUTPUT_ | Getter C1 preheater output
52 | GET_1_BLKT_PID_DATA.SPS | G_1_BKT_PID_DT_SPS | Getter C1 blanket setpoint
53 | GET_1_BLKT_PID_DATA.PV | G_1_VSL_WALL_TEM_ | Getter C1 blanket process variable | <datalog>
54 | GET_1_BLKT_PID_DATA.CVP | G_1_BKT_PID_DT_CVP | Getter C1 blanket output
55 | GET_2_PH_PID_DATA.SPS | G_2_PH_PID_DT_SPS | Getter C2 preheater setpoint
56 | GET_2_PH_PID_DATA.PV | G_2_PH_GAS_TEM_ | Getter C2 preheater process variable | <datalog>
57 | GET_2_PH_PID_DATA.CVP | G_2_PH_SS_OUTPUT_ | Getter C2 preheater output
58 | GET_2_BLKT_PID_DATA.SPS | G_2_BKT_PID_DT_SPS | Getter C2 blanket setpoint
59 | GET_2_BLKT_PID_DATA.PV | G_2_VSL_WALL_TEM_ | Getter C2 blanket process variable | <datalog>
60 | GET_2_BLKT_PID_DATA.CVP | G_2_BKT_PID_DT_CVP | Getter C2 blanket output
61 | GET_3_PH_PID_DATA.SPS | G_3_PH_PID_DT_SPS | Getter C3 preheater setpoint
62 | GET_3_PH_PID_DATA.PV | G_3_PH_GAS_TEM_ | Getter C3 preheater process variable | <datalog>
63 | GET_3_PH_PID_DATA.CVP | G_3_PH_SS_OUTPUT_ | Getter C3 preheater output | <datalog>
64 | GET_3_BLKT_PID_DATA.SPS | G_3_BKT_PID_DT_SPS | Getter C3 blanket setpoint
65 | GET_3_BLKT_PID_DATA.PV | G_3_VSL_WALL_TEM_ | Getter C3 blanket process variable | <datalog>
66 | GET_3_BLKT_PID_DATA.CVP | G_3_BKT_PID_DT_CVP | Getter C3 blanket output
67 | ADS_PH_PID_DATA.SPS | ADS_PH_PID_DT_SPS | Adsorber Preheater PID set point | PID ADS Preheater
68 | ADS_PH_PID_DATA.PV | ADS_PH_GAS_TEM_RD_ | Adsorbers Preheater PID process variable | <datalog>
69 | ADS_PH_PID_DATA.CVP | ADS_PH_PID_DT_CVP | Adsorbers Preheater control output | PID ADS Preheater
70 | ADS_BLKT_PID_DATA.SPS | BLANKET_SP_ | Adsorber wall PID set point | <datalog> CONTROL Blanket PID Setpoint
71 | ADS_BLKT_PID_DATA.PV | ADS_B_WALL_TEM_RD_ | Adsorber wall PID process variable | <datalog>
72 | ADS_BLKT_PID_DATA.CVP | ADS_B_BKT_PID_DT_CVP | Adsorber wall control output | PID ADS B Blanket
73 | H2_LEVEL_PERCENT | H2_LEVEL_PERCENT_ | Hydrogen sensor reading
74 | DIFF_PRESS_TRANS_READ | DIFF_PRES_TRANS_RD_ | DPT-1 cabinet pressure reading
1440 | MB_HEARTBEAT_ON/EN | MB_HB_ON_EN | Flashing bit to indicate values are updating
1441 | ACTIVE_SYSTEM_ALARM | ACT_SYSTEM_ALM_ | System alarm
1442 | ACTIVE_REGEN_ALARM | ACT_RG_ALM_ | Regen alarm
1443 | ACTIVE_PURIFY_ALARM | ACT_PUR_ALM_ | Purify alarm
1444 | WARNING_FLAG |  | Warning indicator
1445 | SYSTEM_STANDBY | SYSTEM_STANDBY_ | System in standby | STATE System Process
1446 | PURIFY_MANUAL_HOLD | PUR_MANUAL_HOLD_ | Manual purify hold command | STATE Purify Manual Hold
1447 | SET_REGEN_HOLD | SET_RG_HOLD_ | Manual regen hold command
1448 | EMO_ACTIVE | EMO_ACT_ | Emergency stop is active | STATUS The EMO has been depressed
1449 | PROC_PURIFY_A | PROC_PFY_A_REG_B_ | Bed A is purifying | STATE Process Purify A
1450 | PROC_PURIFY_B | PROC_PFY_B_REG_A_ | Bed B is purifying | STATE Process Purify B
1451 | ALARM_RELAY_CONFIG | ALM_RLY_CONFIG_ | Alarm relay configuration (0 = standard, 1 = failsafe)
1452 | WATCHDOG | WATCHDOG_ | K9: PLC Watchdog | K9
1453 | ALARM_RELAY | ALM_RLY_ | K10: Alarm relay | K10
1454 | GAS_RELAY | GAS_RLY_ | K11: Gas relay | K11
1456 | AV1 (open) | ADS_A_RG_OUT_ | Adsorber A regeneration gas outlet valve | SV-1 OPEN
1457 | AV2 (open) | ADS_A_PFY_IN_OPEN_ | Adsorber A process gas inlet valve | SV-2 OPEN
1458 | AV3 (open) | ADS_B_PFY_IN_OPEN_ | Adsorber B process gas inlet valve | SV-3 OPEN
1459 | AV4 (open) | ADS_B_RG_OUT_ | Adsorber B regeneration gas outlet valve | SV-4 OPEN
1460 | AV5 (open) | PURIFIED_GAS_OUT_ | Outlet valve | SV-5 OPEN
1461 | AV6 (open) | ADS_A_RG_IN_ | Adsorber A regeneration gas inlet valve | SV-6 OPEN
1462 | AV7 (open) | ADS_A_PFY_OUT_OPEN_ | Adsorber A purified gas outlet valve | SV-7 OPEN
1463 | AV8 (open) | ADS_B_PFY_OUT_OPEN_ | Adsorber B purified gas outlet valve | SV-8 OPEN
1464 | AV9 (open) | ADS_B_RG_IN_ | Adsorber B regeneration gas inlet valve | SV-9 OPEN
1465 | AV10 (open) | MIN_BLEED_FLOW_VLV_ | Minimum bleed flow valve | SV-10 OPEN
1466 | AV11 (open) | SYSTEM_PURG_IN_ | Argon system purge valve | SV-11 OPEN
1467 | AV12 (open) | RG_VENT_PURG_VLV_ | Regeneration vent argon purge valve | SV-12 OPEN
1468 | AV13 (open) | RG_GAS_IN_ | Regeneration gas inlet valve | SV-13 OPEN
1469 | AV14 (open) | STARTUP_H2_IN_ | Cold start gas inlet valve | SV-14 OPEN
1470 | AV15 | BYPASS_VLV_ | Bypass valve (1 = autobypass closed, PMAN open) | BYPASS
1471 | AV16 (open) | ARGON_SUPPLY_VLV_ | Argon supply valve | SV-16 OPEN
1472 | GETT_ROD_CONTACTOR | GETT_ROD_CTR_ | K1~K3: Getter rod heating contactors | K1~K3
1473 | GETT_SHELL_CONTACTOR | GETT_SHELL_CTR_ | K4~K6: Getter shell heating contactors | K4~K6
1474 | GET_1_BLKT_SSR | G_1_BKT_SSR_ | SSR4: Getter 1 blanket heater | SSR4
1475 | GET_2_BLKT_SSR | G_2_BKT_SSR_ | SSR5: Getter 2 blanket power | SSR5
1476 | GET_3_BLKT_SSR | G_3_BKT_SSR_ | SSR6: Getter 3 blanket power | SSR6
1477 | GET_1_PH_SSR | G_1_PH_SSR_ | SSR1: Getter 1 preheater power | SSR1
1478 | GET_2_PH_SSR | G_2_PH_SSR_ | SSR2: Getter 2 preheater power | SSR2
1479 | GET_3_PH_SSR | G_3_PH_SSR_ | SSR3: Getter 3 preheater power | SSR3
1480 | ADS_A_CONTACTOR | ADS_A_CTR_ | K7: Adsorber A heating contactor | K7
1481 | ADS_B_CONTACTOR | ADS_B_CTR_ | K8: Adsorber B heating contactor | K8
1482 | ADS_PH_CONTACTOR | ADS_PH_CTR_ | K9: Adsorber A&B heating contactor | K9
1483 | ADS_BLANKET_SSR | ADS_BLANKET_SSR_ | SSR7~8: Getter blanket power | SSR7~8
1484 | ADS_PREHEATER_SSR | ADS_PREHEATER_SSR_ | SSR9~10: Getter preheater power | SSR9~10
1489 | PLC_FAULT_ALARM | PLC_FAULT_ALM_ | Major PLC Fault alarm
1490 | UPS_FAULTED_ALARM | UPS_FAULTED_ALM_ | Uninterrupted Power Supply failure alarm
1491 | X_PURGE_FAIL_ALARM | X_PURG_FAIL_ALM_ | Pressure lost on X-Purge system alarm
1493 | LF_PURGE_ALARM | LF_PURG_ALM_ | Low purge flow alarm
1494 | OPEN_TC16_ALARM | OPEN_TC16_ALM_ | TC16 Open alarm
1495 | LP_ARGON_ALARM | LP_ARGON_ALM_ | Low argon pressure alarm
1496 | H2_PURGE_FAIL_ALARM | H2_PURG_FAIL_ALM_ | Argon cycle purge incomplete alarm
1497 | LOW_PLC_BATTERY_ALM | LOW_PLC_BATT_ALM_ | Low PLC Battery alarm | ALARM System Low PLC Battery
1498 | GFI_TRIPPED_ALARM | GFI_TRIPPED_ALM_ | Ground fault indicator tripped alarm | ALARM System GFI Tripped
1499 | MAIN_PWR_ALARM | MAIN_PWR_ALM_ | Power failure alarm | ALARM System Main Power Fail
1500 | CTL_PWR_ALARM | CTL_PWR_ALM_ | Control power failure alarm | ALARM System Control Power Fail
1501 | PURIFY_HOLD_ALARM | PUR_HOLD_ALM_ | Purify holding alarm | ALARM System Purify Hold
1502 | LP_INLET_GAS_ALARM | LP_INLET_GAS_ALM_ | Low Pressure Gas Inlet alarm
1503 | HP_GAS_ALARM | HP_GAS_ALM_ | High System Gas Pressure alarm | ALARM Gas Inlet High Pressure
1504 | Z_PURGE_FAIL_ALARM | Z_PURG_FAIL_ALM_ | Pressure lost on Z-Purge system alarm
1505 | OPEN_PX1_ALARM | OPEN_PX1_ALM_ | Pressure transducer 1 open alarm | ALARM Gas Inlet Pressure Transmitter Broken
1506 | OPEN_PX2_ALARM | OPEN_PX2_ALM_ | Pressure transducer 2 open alarm | ALARM Gas Outlet Pressure Transmitter Broken
1507 | LP_OUT_GAS_ALARM | LP_OUT_GAS_ALM_ | Low outlet gas pressure alarm
1508 | SAFETY_VENT_ALARM | SAFETY_VENT_ALM_ | Overpressure Event alarm
1509 | ARGON_LEAK_ALARM | ARGON_LEAK_ALM_ | Argon purge leak alarm
1510 | LF_WATER_ALARM | LF_WATER_ALM_ | Low water flow alarm
1511 | LP_CABINET_ALARM | LP_CABINET_ALM_ | Low electrical cabinet pressure alarm
1512 | GET_HT_OUT_GAS_ALARM | G_HT_OUT_GAS_ALM_ | High temperature outlet gas alarm
1513 | GET_LT_BED_ALARM | G_LT_BED_ALM_ | Low temperature getter bed alarm
1514 | OPEN_PX3_ALARM | OPEN_PX3_ALM_ | Pressure transducer 3 open alarm
1515 | OPEN_PX4_ALARM | OPEN_PX4_ALM_ | Pressure transducer 4 open alarm
1516 | LOW_AIR_FLOW_ALARM | LOW_AIR_FLOW_ALM_ | Low air flow alarm
1517 | LP_EXT_PNEU_ALARM | LP_EXT_PNEU_ALM_ | Low external pneumatic pressure alarm | ALARM System Pneumatic Pressure Low
1518 | LP_INT_PNEU_ALARM | LP_INT_PNEU_ALM_ | Low internal pneumatic pressure alarm
1536 | HTI_ALARM | HTI_ALM_ | Adsorber heater interlock alarm | ALARM High Temperature Interlocks
1537 | PH_FAULT_ALARM | PH_FAULT_ALM_ | Adsorber PH failed to heat alarm | ALARM Preheater Fault
1540 | VENT_FAIL_ALARM | VENT_FAIL_ALM_ | No vent in regen alarm
1541 | BACKFILL_FAIL_ALARM | BACKFILL_FAIL_ALM_ | No backfill in regen alarm
1542 | LOW_GAS_DEV_ALARM | LOW_GAS_DEV_ALM_ | Low regen gas deviation alarm
1543 | HI_GAS_DEV_ALARM | HI_GAS_DEV_ALM_ | High regen gas deviation alarm
1547 | REG_COOL_FAIL_ALARM | REG_COOL_FAIL_ALM_ | Adsorber cooling failure alarm
1548 | OPEN_TC17_ALARM | OPEN_TC17_ALM_ | Open TC17 alarm
1549 | OPEN_TC18_ALARM | OPEN_TC18_ALM_ | Open TC18 alarm
1550 | HT_PH_GAS_ALARM | HT_PH_GAS_ALM_ | High temperature adsorber preheater gas alarm
1551 | HT_PH_ROD_ALARM | HT_PH_ROD_ALM_ | High temperature adsorber preheater alarm
1553 | OPEN_TC20_ALARM | OPEN_TC20_ALM_ | Open TC20 alarm | ALARM Adsorber A Bed Thermocouple Open
1555 | OPEN_TC19_ALARM | OPEN_TC19_ALM_ | Open TC19 alarm | ALARM Adsorber A Wall Thermocouple Open
1557 | HT_WALL_ADS_A_ALARM | HT_WALL_ADS_A_ALM_ | High temperature adsorber wall alarm | ALARM ADS A REGEN Wall High Temp
1558 | LT_BED_ADS_A_ALARM | LT_BED_ADS_A_ALM_ | Low temp on adsorber bed A alarm | ALARM ADS A Wall Low Temperature
1560 | HT_BED_ADS_A_ALARM | HT_BED_ADS_A_ALM_ | High temperature adsorber A bed alarm
1568 | ADS_A_HT_PURIFY_ALM | ADS_A_HT_PUR_ALM_ | High temperature on purify A bed alarm | ALARM ADS A Purify High Temp
1585 | OPEN_TC22_ALARM | OPEN_TC22_ALM_ | Open TC22 alarm | ALARM Adsorber B Bed Thermocouple Open
1587 | OPEN_TC21_ALARM | OPEN_TC21_ALM_ | Open TC21 alarm | ALARM Adsorber B Wall Thermocouple Open
1589 | HT_WALL_ADS_B_ALARM | HT_WALL_ADS_B_ALM_ | High temperature adsorber B wall alarm | ALARM ADS B REGEN Wall High Temp
1590 | LT_BED_ADS_B_ALARM | LT_BED_ADS_B_ALM_ | Low temp on adsorber bed B alarm | ALARM ADS B Wall Low Temperature
1592 | HT_BED_ADS_B_ALARM | HT_BED_ADS_B_ALM_ | High temperature adsorber B bed alarm
1600 | ADS_B_HT_PURIFY_ALM | ADS_B_HT_PUR_ALM_ | High temperature on purify B bed alarm | ALARM ADS B Purify High Temp
1616 | SCREEN_COMMS_ERROR | SCREEN_COMMS_ERR_ | HMI lost communication warning
1617 | MODBUS_ERROR | MODBUS_ERR_ | Modbus gateway communication error warning
1618 | UPS_FAULTED_WARN | UPS_FAULTED_WRN_ | Uninterrupted Power Supply failure warning
1619 | Z_PURGE_FAIL_WARN | Z_PURG_FAIL_WRN_ | Pressure lost on Z-Purge system warning
1620 | X_PURGE_FAIL_WARN | X_PURG_FAIL_WRN_ | Pressure lost on X-Purge system warn
1621 | LF_PURGE_WARN | LF_PURG_WRN_ | Low purge flow warning
1622 | OPEN_TC16_WARN | OPEN_TC16_WRN_ | TC16 Open warning
1623 | LP_ARGON_WARN | LP_ARGON_WRN_ | Low argon pressure warning
1624 | H2_PURGE_FAIL_WARN | H2_PURG_FAIL_WRN_ | Argon cycle purge incomplete warning
1625 | LOW_PLC_BATTERY_WARN | LOW_PLC_BATT_WRN_ | Low PLC battery warning | WARNING System Low PLC Battery
1626 | GFI_TRIPPED_WARN | GFI_TRIPPED_WRN_ | Ground fault indicator tripped warning | WARNING System GFI Tripped
1627 | MAIN_PWR_WARN | MAIN_PWR_WRN_ | Power failure warning | WARNING System Control Power Fail
1628 | CTL_PWR_WARN | CTL_PWR_WRN_ | Control power failure warning | WARNING System Control Power Fail
1629 | PURIFY_HOLD_WARN | PUR_HOLD_WRN_ | Purify holding warning | WARNING System Purify Hold
1630 | LP_INLET_GAS_WARN | LP_INLET_GAS_WRN_ | Low pressure gas inlet warning
1631 | HP_GAS_WARN | HP_GAS_WRN_ | High system gas pressure warning | WARNING Gas Inlet High Pressure
1633 | OPEN_PX1_WARN | OPEN_PX1_WRN_ | Pressure transducer 1 open warning | WARNING Gas Inlet Pressure Transmitter Broken
1634 | OPEN_PX2_WARN | OPEN_PX2_WRN_ | Pressure transducer 2 open warning | WARNING Gas Outlet Pressure Transmitter Broken
1635 | LP_OUT_GAS_WARN | LP_OUT_GAS_WRN_ | Low outlet gas pressure warning
1636 | SAFETY_VENT_WARN | SAFETY_VENT_WRN_ | Overpressure event warning
1637 | ARGON_LEAK_WARN | ARGON_LEAK_WRN_ | Argon purge leak warning
1638 | LF_WATER_WARN | LF_WATER_WRN_ | Low water flow warning
1639 | LP_CABINET_WARN | LP_CABINET_WRN_ | Low electrical cabinet pressure warning
1640 | GET_HT_OUT_GAS_WARN | G_HT_OUT_GAS_WRN_ | High temperature outlet gas warning
1641 | GET_LT_BED_WARN | G_LT_BED_WRN_ | Low temperature getter bed warning
1642 | OPEN_PX3_WARN | OPEN_PX3_WRN_ | Pressure transducer 3 open warning
1643 | OPEN_PX4_WARN | OPEN_PX4_WRN_ | Pressure transducer 4 open warning
1644 | LOW_AIR_FLOW_WARN | LOW_AIR_FLOW_WRN_ | Low air flow warning
1645 | LP_EXT_PNEU_WARN | LP_EXT_PNEU_WRN_ | Low external pneumatic pressure warning | WARNING System Pneumatic Pressure Low
1646 | LP_INT_PNEU_WARN | LP_INT_PNEU_WRN_ | Low internal pneumatic pressure warning
1664 | HTI_WARN | HTI_WRN_ | Adsorber heater interlock warning | WARNING High Temperature Interlocks
1665 | PH_FAULT_WARN | PH_FAULT_WRN_ | Adsorber PH failed to heat warning | WARNING Preheater Fault
1668 | VENT_FAIL_WARN | VENT_FAIL_WRN_ | No vent in regen warning
1669 | BACKFILL_FAIL_WARN | BACKFILL_FAIL_WRN_ | No backfill in regen warning
1670 | LOW_GAS_DEV_WARN | LOW_GAS_DEV_WRN_ | Low regen gas deviation warning
1671 | HI_GAS_DEV_WARN | HI_GAS_DEV_WRN_ | High regen gas deviation warning
1675 | REG_COOL_FAIL_WARN | REG_COOL_FAIL_WRN_ | Adsorber cooling failure warning
1676 | OPEN_TC17_WARN | OPEN_TC17_WRN_ | Open TC17 warning
1677 | OPEN_TC18_WARN | OPEN_TC18_WRN_ | Open TC18 warning
1678 | HT_PH_GAS_WARN | HT_PH_GAS_WRN_ | High temperature adsorber preheater gas warning
1679 | HT_PH_ROD_WARN | HT_PH_ROD_WRN_ | High temperature adsorber preheater warning
1681 | OPEN_TC20_WARN | OPEN_TC20_WRN_ | Open TC20 warning | WARNING Adsorber A Bed Thermocouple Open
1683 | OPEN_TC19_WARN | OPEN_TC19_WRN_ | Open TC19 warning | WARNING Adsorber A Wall Thermocouple Open
1685 | HT_WALL_ADS_A_WARN | HT_WALL_ADS_A_WRN_ | High temperature adsorber wall warning | WARNING ADS A Wall High Temperature
1686 | LT_BED_ADS_A_WARN | LT_BED_ADS_A_WRN_ | Low temp on adsorber bed A warning | WARNING ADS A Wall Low Temperature
1688 | HT_BED_ADS_A_WARN | HT_BED_ADS_A_WRN_ | High temperature adsorber A bed warning
1696 | ADS_A_HT_PURIFY_WARN | ADS_A_HT_PUR_WRN_ | High temperature on purify A bed warning | WARNING ADS A Purify High Temp
1713 | OPEN_TC22_WARN | OPEN_TC22_WRN_ | Open TC22 warning | WARNING Adsorber B Bed Thermocouple Open
1715 | OPEN_TC21_WARN | OPEN_TC21_WRN_ | Open TC21 warning | WARNING Adsorber B Wall Thermocouple Open
1717 | HT_WALL_ADS_B_WARN | HT_WALL_ADS_B_WRN_ | High temperature adsorber B wall warning | WARNING ADS B Wall High Temperature
1718 | LT_BED_ADS_B_WARN | LT_BED_ADS_B_WRN_ | Low temp on adsorber bed B warning | WARNING ADS B Wall Low Temperature
1720 | HT_BED_ADS_B_WARN | HT_BED_ADS_B_WRN_ | High temperature adsorber B bed warning
1728 | ADS_B_HT_PURIFY_WARN | ADS_B_HT_PUR_WRN_ | High temperature on purify B bed warning | WARNING ADS B Purify High Temp
1744 | GET_1_HT_PH_GAS_ALM | G_1_HT_PH_GAS_ALM_ | Getter C1 high preheater gas temp alarm
1745 | GET_1_HT_PH_ALARM | G_1_HT_PH_ALM_ | Getter C1 high preheater temp alarm
1746 | GET_1_HT_BED_ALARM | G_1_HT_BED_ALM_ | Getter C1 high preheater bed alarm
1747 | GET_1_HT_WALL_ALARM | G_1_HT_WALL_ALM_ | Getter C1 high preheater wall alarm
1749 | GET_1_HTI_ALARM | G_1_HTI_ALM_ | Getter C1 interlock alarm
1760 | OPEN_TC1_ALARM | OPEN_TC1_ALM_ | Open TC1 alarm
1761 | OPEN_TC2_ALARM | OPEN_TC2_ALM_ | Open TC2 alarm
1762 | OPEN_TC3_ALARM | OPEN_TC3_ALM_ | Open TC3 alarm
1763 | OPEN_TC4_ALARM | OPEN_TC4_ALM_ | Open TC4 alarm
1764 | OPEN_TC5_ALARM | OPEN_TC5_ALM_ | Open TC5 alarm
1776 | GET_2_HT_PH_GAS_ALM | G_2_HT_PH_GAS_ALM_ | Getter C2 high preheater gas temp alarm
1777 | GET_2_HT_PH_ALARM | G_2_HT_PH_ALM_ | Getter C2 high preheater temp alarm
1778 | GET_2_HT_BED_ALARM | G_2_HT_BED_ALM_ | Getter C2 high preheater bed alarm
1779 | GET_2_HT_WALL_ALARM | G_2_HT_WALL_ALM_ | Getter C2 high preheater wall alarm
1781 | GET_2_HTI_ALARM | G_2_HTI_ALM_ | Getter C2 interlock alarm
1792 | OPEN_TC6_ALARM | OPEN_TC6_ALM_ | Open TC6 alarm
1793 | OPEN_TC7_ALARM | OPEN_TC7_ALM_ | Open TC7 alarm
1794 | OPEN_TC8_ALARM | OPEN_TC8_ALM_ | Open TC8 alarm
1795 | OPEN_TC9_ALARM | OPEN_TC9_ALM_ | Open TC9 alarm
1796 | OPEN_TC10_ALARM | OPEN_TC10_ALM_ | Open TC10 alarm
1808 | GET_3_HT_PH_GAS_ALM | G_3_HT_PH_GAS_ALM_ | Getter C3 high preheater gas temp alarm
1809 | GET_3_HT_PH_ALARM | G_3_HT_PH_ALM_ | Getter C3 high preheater temp alarm
1810 | GET_3_HT_BED_ALARM | G_3_HT_BED_ALM_ | Getter C3 high preheater bed alarm
1811 | GET_3_HT_WALL_ALARM | G_3_HT_WALL_ALM_ | Getter C3 high preheater wall alarm
1813 | GET_3_HTI_ALARM | G_3_HTI_ALM_ | Getter C3 interlock alarm
1824 | OPEN_TC11_ALARM | OPEN_TC11_ALM_ | Open TC11 alarm
1825 | OPEN_TC12_ALARM | OPEN_TC12_ALM_ | Open TC12 alarm
1826 | OPEN_TC13_ALARM | OPEN_TC13_ALM_ | Open TC13 alarm
1827 | OPEN_TC14_ALARM | OPEN_TC14_ALM_ | Open TC14 alarm
1828 | OPEN_TC15_ALARM | OPEN_TC15_ALM_ | Open TC15 alarm
1840 | GET_1_HT_PH_GAS_WRN | G_1_HT_PH_GAS_WRN_ | Getter C1 high preheater gas temp warning
1841 | GET_1_HT_PH_WARN | G_1_HT_PH_WRN_ | Getter C1 high preheater temp warning
1842 | GET_1_HT_BED_WARN | G_1_HT_BED_WRN_ | Getter C1 high preheater bed warning
1843 | GET_1_HT_WALL_WARN | G_1_HT_WALL_WRN_ | Getter C1 high preheater wall warning
1845 | GET_1_HTI_WARN | G_1_HTI_WRN_ | Getter C1 interlock warning
1860 | OPEN_TC5_WARN | OPEN_TC5_WRN_ | Open TC5 warning
1872 | GET_2_HT_PH_GAS_WRN | G_2_HT_PH_GAS_WRN_ | Getter C2 high preheater gas temp warning
1873 | GET_2_HT_PH_WARN | G_2_HT_PH_WRN_ | Getter C2 high preheater temp warning
1874 | GET_2_HT_BED_WARN | G_2_HT_BED_WRN_ | Getter C2 high preheater bed warning
1875 | GET_2_HT_WALL_WARN | G_2_HT_WALL_WRN_ | Getter C2 high preheater wall warning
1877 | GET_2_HTI_WARN | G_2_HTI_WRN_ | Getter C2 interlock warning
1892 | OPEN_TC10_WARN | OPEN_TC10_WRN_ | Open TC10 warning
1904 | GET_3_HT_PH_GAS_WRN | G_3_HT_PH_GAS_WRN_ | Getter C3 high preheater gas temp warning
1905 | GET_3_HT_PH_WARN | G_3_HT_PH_WRN_ | Getter C3 high preheater temp warning
1906 | GET_3_HT_BED_WARN | G_3_HT_BED_WRN_ | Getter C3 high preheater bed warning
1907 | GET_3_HT_WALL_WARN | G_3_HT_WALL_WRN_ | Getter C3 high preheater wall warning
1909 | GET_3_HTI_WARN | G_3_HTI_WRN_ | Getter C3 interlock warning
1924 | OPEN_TC15_WARN | OPEN_TC15_WRN_ | Open TC15 warning
1936 | H2_LEAK_ALARM | H2_LEAK_ALM_ | Hydrogen leak alarm
1952 | H2_LEAK_WARN | H2_LEAK_WRN_ | Hydrogen leak warning
1953 | H2_LEVEL_WARN | H2_LEVEL_WRN_ | High hydrogen level warning
1954 | H2_SENS_START_DELAY | H2_SENS_START_DELAY_ | Hydrogen start delay sensor | Hydrogen Sensor Start Up Delay
1968 | MAIN_PWR_FAIL_RELAY | MAIN_PWR_FAIL_RLY_ | Main Power Fail Relay | K7
1969 | CNTRL_PWR_FAIL_RELAY | CNTRL_PWR_FAIL_RLY_ | Contrl Power Fail Relay | K8
1970 | DIFF_PRESS_SWITCH | DIFF_PRESS_SWITCH_ | Differential Pressure Switch
1974 | X_PURGE_OK | X_PURG_OK_ | X Purge ok
1975 | Z_PURGE_ALARM | Z_PURG_ALM_ | K2 - Z Purge alarm | K2 - Normally closed. Inverse of K1 to provide a failsafe signal from Z-purge unit.
1976 | X_PURGE_IN_PROCESS | X_PURG_IN_PROCESS_ | AUX1 - X Purge in process | AUX 1 - Signal high when X-purge is purging. Normally open contact.
1978 | Z_PURGE_OK | Z_PURG_OK_ | K1 - Z Purge ok | K1 - Normally Open. Signal high when Z- purge conditions are satisfied.